|  | DEPARTMENT OF VETERANS AFFAIRS |  |
| --- | --- | --- |
|  | VHA MASTER SPECIFICATIONS |  |
|  | TABLE OF CONTENTS Section 00 01 10 |  |
|  | DIVISION 00 - SPECIAL SECTIONS | DATE |
| 00 01 15 | List of Drawing Sheets | 05-20 |
|  | DIVISION 01 - GENERAL REQUIREMENTS |  |
| 01 00 00 | General Requirements | 05-21 |
| 01 32 16 | Project Schedule | 03-20 |
| 01 33 23 | Shop Drawings, Product Data, and Samples | 06-21 |
| 01 35 26 | Safety Requirements | 07-20 |
| 01 42 19 | Reference Standards | 11-20 |
| 01 45 00 | Quality Control | 02-21 |
| 01 45 29 | Testing Laboratory Services | 11-18 |
| 01 45 35 | Special Inspection | 06-21 |
| 01 57 19 | Temporary Environmental Controls | 01-11 |
| 01 74 19 | Construction Waste Management | 01-21 |
| 01 81 13 | Sustainable Construction Requirements | 10-17 |
| 01 91 00 | General Commissioning Requirements | 10-15 |
|  | DIVISION 02 – EXISTING CONDITIONS |  |
| 02 41 00 | Demolition | 08-17 |
| 02 82 11 | Asbestos Abatement Specifications | 01-21 |
| 02 83 33.13 | Lead-Based Paint Removal and Disposal | 01-21 |
|  | DIVISION 03 – CONCRETE |  |
| 03 30 00 | Cast-in-Place Concrete | 01-21 |
|  | DIVISION 04 – MASONRY |  |
| 04 05 13 | Masonry Mortaring | 10-17 |
| 04 05 16 | Masonry Grouting | 01-21 |
| 04 20 00 | Unit Masonry | 08-17 |
| 04 72 00 | Cast Stone Masonry |  |
|  | DIVISION 05 – METALS |  |
| 05 50 00 | Metal Fabrications | 08-18 |
|  | DIVISION 06 - CARPENTRY |  |
| 06 10 00 | Rough Carpentry | 10-17 |
|  | DIVISION 07 - THERMAL AND MOISTURE PROTECTION |  |
| 07 21 13 | Thermal Insulation | 01-21 |
| 07 22 00 | Roof and Deck Insulation | 01-21 |
| 07 53 23 | Ethylene-Propylene-Diene-Monomer Roofing | 01-21 |
| 07 60 00 | Flashing and Sheet Metal | 01-21 |
| 07 84 00 | Fire Stopping | 01-21 |
| 07 92 00 | Joint Sealants | 10-17 |
|  | DIVISION 08 - OPENINGS |  |
| 08 11 13 | Hollow Metal Doors and Frames | 01-21 |
| 08 14 00 | Interior Wood Doors | 01-21 |
| 08 51 13 | Aluminum Window | 01-21 |
| 08 71 00 | Door Hardware | 01-21 |
| 08 80 00 | Glazing | 01-21 |
|  | DIVISION 09 – FINISHES |  |
| 09 06 00 | Schedule for Finishes | 01-21 |
| 09 22 16 | Non-Structural Metal Framing | 06-18 |
| 09 29 00 | Gypsum Board | 04-20 |
| 09 51 00 | Acoustical Ceilings | 12-18 |
| 09 65 13 | Resilient Base and Accessories | 01-21 |
| 09 91 00 | Painting | 01-21 |
|  | DIVISION 10 – SPECIALTIES |  |
| 10 26 00 | Wall and Door Protection | 01-21 |
| 10 44 13 | Fire Extinguisher Cabinets | 08-18 |
|  | DIVISION 13 - SPECIAL CONSTRUCTION |  |
| 13 05 41 | Seismic Restraint Requirement | 01-21 |
|  | DIVISION 21- FIRE SUPPRESSION |  |
| 21 08 00 | Commissioning of Fire Suppression System | 11-16 |
| 21 13 13 | Wet-Pipe Sprinkler Systems | 06-15 |
|  | DIVISION 22 – PLUMBING |  |
| 22 05 11 | Common Work Results for Plumbing | 09-20 |
| 22 05 23 | General-Duty Valves for Plumbing Piping | 09-20 |
| 22 07 11 | Plumbing Insulation | 09-15 |
| 22 11 00 | Facility Water Distribution | 05-21 |
| 22 13 00 | Facility Sanitary and Vent Piping | 09-20 |
| 22 14 00 | Facility Storm Drainage | 09-15 |
|  | DIVISION 23 – HEATING, VENTILATING, AND AIR CONDITIONING (HVAC) |  |
| 23 05 11 | Common Work Results for HVAC | 02-20 |
| 23 05 12 | General Motor Requirements for HVAC and Steam Generation Equipment | 02-20 |
| 23 05 41 | Noise and Vibration Control for HVAC Piping and Equipment | 02-20 |
| 23 05 93 | Testing, Adjusting, and Balancing for HVAC | 02-20 |
| 23 07 11 | HVAC and Boiler Plant Insulation | 02-20 |
| 23 08 00 | Commissioning of HVAC Systems | 02-20 |
| 23 22 13 | Steam and Condensate Heating Piping | 02-20 |
| 23 22 13 | Steam and Condensate Heating Piping | 02-20 |
| 23 23 00 | Refrigerant Piping | 02-20 |
| 23 31 00 | HVAC Ducts and Casings | 02-20 |
| 23 34 00 | HVAC Fans | 02-20 |
| 23 36 00 | Air Terminal Units | 02-20 |
| 23 37 00 | Air Outlets and Inlets | 02-20 |
| 23 73 00 | Indoor Central-Station Air-Handling Units | 03-20 |
|  | DIVISION 26 – ELECTRICAL |  |
| 26 05 11 | Requirements for Electrical Installations | 01-16 |
| 26 05 19 | Low-Voltage Electrical Power Conductors and Cables | 01-17 |
| 26 05 26 | Grounding and Bonding for Electrical Systems | 01-17 |
| 26 05 33 | Raceway and Boxes for Electrical Systems | 01-18 |
| 26 08 00 | Commissioning of Electrical Systems | 11-16 |
| 26 09 23 | Lighting Controls | 01-18 |
| 26 24 16 | Panel-boards | 01-18 |
| 26 27 26 | Wiring Devices | 01-18 |
| 26 29 21 | Enclosed Switches and Circuit Breakers | 01-17 |
| 26 51 00 | Interior Lighting | 01-18 |
|  | DIVISION 27 – COMMUNICATIONS |  |
| 27 05 11 | Requirements for Communications Installations | 06-15 |
| 27 05 26 | Grounding and Bonding for Communication Systems | 06-15 |
| 27 05 33 | Raceways and Boxes for Communications Systems | 10-18 |
| 27 08 00 | Commissioning of Communications Systems | 11-16 |
| 27 10 00 | Control, Communications and Signal Wiring | 06-15 |
| 27 11 00 | Communications Equipment Room Fittings | 06-15 |
| 27 15 00 | Communications and Structured Cabling |  |
| 27 51 16 | Public Address and Mass Notification Systems | 10-18 |
|  | DIVISION 28 – ELECTRONIC SAFETY AND SECURITY |  |
| 28 05 00 | Common Work Results for Electronic Safety and Security | 04-18 |
| 28 05 13 | Conductors and Cables for Electronic Safety and Security | 10-18 |
| 28 05 26 | Grounding and Bonding for Electronic Safety and Security | 09-11 |
| 28 08 28.33 | Conduits and Backboxes for Electronic Safety and Security | 09-11 |
| 28 31 00 | Fire Detection and Alarm | 10-11 |

SECTION 00 01 15
LIST OF DRAWING SHEETS

(SAMPLE LIST OF DRAWINGS)

The drawings listed below accompanying this specification form a part of the contract.

Drawing No.				Title

GENERAL INFORMATION DRAWINGS

GI 000	COVERSHEET

GI 001	GENERAL NOTES & REQUIREMENTS

GP 100	GENERAL PHASING PLANS

LS 100	CRITICAL PATH & LIFE SAFETY NOTES

SITE DRAWINGS

SP 100	SITE AN UTILITY PLAN

ASBESTOS ABATEMENT DRAWINGS

HA 100	ASBESTOS ABATEMENT PLAN - ROOF

HA 101	ASBESTOS ABATEMENT PLAN - GROUND FLOOR

HA 102	ASBESTOS ABATEMENT DIAGRAM AND NOTES

ARCHITECTURAL DRAWINGS

AD 000	AD 000	ARCH. NOTES, ABBREV., & SYMBOLS LEGEND

AD 100	ARCHITECTURAL ROOF DEMOLITION PLAN

AD 101	ARCHITECTURAL INTERIOR DEMOLITION

AD 102	REFLECTED CEILING DEMOLITION

AD 201	EXTERIOR ELEVATIONS DEMOLITION

AI 100	NEW ROOF PLAN

AI 101	NEW ARCHITECTURAL INTERIOR PLAN

AI 102 	NEW REFLECTED CEILING PLAN

AI 200	NEW INTERIOR ELEVATIONS

AI 201	NEW EXTERIOR ELEVATIONS

AD 0	AI 400	NEW ENLARGE PLANS

AI 500	NEW ROOF DETAILS

AI 501	NEW ARCHITECTURAL PARTITION DETAILS

AI 502		NEW ARCH. DOOR SCHEDULE, ELEVATIONS, & DOOR

FRAMING DETAIL

AI 600	NEW FINISH SCHEDULE

MECHANICAL DRAWINGS

MI 000	MECH. NOTES, ABBREV., & SYMBOLS

MD 100	EXISTING STEAM DISTRIBUTION AND HEATING

DEMOLITION PLAN

MD 101	EXISTING HVAC DEMOLITION PLAN

MD 102	EXISTING EQUIPMENT DEMO. PLAN

MD 500	EXISTING STEAM DISTRIBUTION SYSTEM DETAILS

ME 100	NEW STEAM DISTRIBUTION PLANS

ME 101	NEW HVAC PLAN

ME 102	NEW EQUIPMENT LOCATION PLAN

ME 500	NEW STEAM DIST. DETAILS

ME 501	NEW HVAC DETAILS

ME 502	NEW HVAC CONTROLS INFORMATION

ME 600	NEW HVAC SCHEDULES

ELECTRICAL DRAWINGS

EI 100	ELECTRICAL NOTES, ABBREV., & SYMBOLS LEGEND

ED 100	ELECTRICAL POWER DEMOLITION PLAN

ED 101	ELECTRICAL LIGHTING DEMOLITION

ED 600	ELECTRICAL DEMOLITION ONE-LINE DIAGRAM

ED 601	ELECTRICAL DEMOLITION EXISTING PANEL SCHEDULE

EP 100	NEW ELECTRICAL POWER DISTRIBUTION PLAN

EP 120	NEW ELECTRICAL RECEPTACLE WIRING PLAN

EP 130	NEW ELECTRICAL LIGHTING WIRING PLAN

EP 140	NEW ELECTRICAL EMERGENCY POWER WIRING PLAN

EP 600	NEW ELECTRICAL ONE-LINE DIAGRAM

EL 100	ELECTRICAL LIGHTING PLAN

ES 601	NEW PANEL SCHEDULES

PLUMBING DRAWINGS

MI 000	MECH. NOTES, ABBREV., & SYMBOLS LEGEND

PD 100	EXISTING SANITARY DEMOLITION PLAN

PD 101	EXISTING DOMW DEMOLITION PLAN

PD 200	EXISTING DOMW INTERIOR SECTION ELEVATION

DEMOLITION

PD 300	EXISTING DETAILS

PL 100	NEW SANITARY PLAN

PL 101	NEW DOMW PLAN

PL 500	NEW PLUMBING DETAILS

FIRE PROTECTION & SUPPRESSION DRAWINGS

FI 000	FIRE PROTECTION ABBREV. & SYMBOLS LEGEND

FI 001	FIRE PROTECTION GENERAL NOTES

FD 100	FIRE ALARM DEMOLITION PLANS

FD 101	FIRE SUPPRESSION DEMOLITION PLAN & SITE DETAILS

FA 100	NEW FIRE ALARM PLANS

FX 100	NEW FIRE SUPPRESSION PLAN

AD

30-6	Schedules

- - - E N D - - -

SECTION 01 00 00
GENERAL REQUIREMENTS

TABLE OF CONTENTS

1.1 SAFETY REQUIREMENTS	1

1.2 GENERAL INTENTION	1

1.3 STATEMENT OF BID ITEM(S)	1

1.4 SPECIFICATIONS AND DRAWINGS FOR CONTRACTOR	2

1.5 CONSTRUCTION SECURITY REQUIREMENTS	2

1.6 OPERATIONS AND STORAGE AREAS	5

1.7 ALTERATIONS	8

1.8 RESTORATION	10

1.9 PHYSICAL DATA	11

1.10 LAYOUT OF WORK	11

1.11 AS-BUILT DRAWINGS	11

1.13 TEMPORARY TOILETS	12

1.14 AVAILABILITY AND USE OF UTILITY SERVICES	13

1.15 TESTS	14

1.16 INSTRUCTIONS	15

1.17 RELOCATED EQUIPMENT AND ITEMS 	16

1.18 CONSTRUCTION SIGN	17

1.19 SAFETY SIGN	17

1.20 HISTORIC PRESERVATION	18

SECTION 01 00 00
GENERAL REQUIREMENTS

1.1 safety requirements

Refer to section 01 35 26, SAFETY REQUIREMENTS for safety and infection control requirements.

1.2 GENERAL INTENTION

A.	Contractor shall completely prepare site for building operations, including demolition and removal of existing structures, and furnish labor and materials and perform work for Project 620-20-206 “Fire Department Renovations at FDR” as required by drawings and specifications.

B.	Visits to the site by Bidders may be made only by appointment with the Medical Center Engineering.

C.	All employees of general contractor and subcontractors shall comply with VA security management program and obtain permission of the VA police, be identified by project and employer, and restricted from unauthorized access.

1.3 STATEMENT OF BID ITEM(S)

A.	ITEM I, GENERAL CONSTRUCTION: BASE BID:  The Contractor shall furnish all labor, materials, tools equipment and supervision necessary to perform and complete the work for the Project #620-20-206, Building 19 Fire Department Building Renovation at the FDR Montrose Campus. The renovations will include but not be limited to the project phasing for the demolition and general interior alterations, Lead and Asbestos abatement, Roof System replacement, Mechanical and Plumbing system upgrades and all Electrical system upgrades in strict accordance with the contract drawings , specifications and any applicable codes at the Montrose, VA Hudson Valley Healthcare System, New York.

Work shall comply with VA Specifications and Regulations, specific regulations related to working at VA Hudson valley Health Care System, Montrose, New York as defined in the General Requirements Section of the contract, and all applicable Federal, State and Local codes.  Contractor shall be responsible to complete the work within the contractual period of performance, and typically within the work hours as defined in the contract. The Contractor shall anticipate performing some of this work during non-peak hours, such as weekends or evenings to accommodate activities at this site. Contractor shall be responsible to plan and coordinate Construction Phasing with the Project Engineer/COR to ensure full access to the site at all times.

Asbestos and Lead abatement: Asbestos and Lead abatement within Building 19.

Project will involve but not be limited to trades such as asbestos abatement, lead paint abatement, disposal of abatement wastes.  The period of performance for this project will include the following elements as noted below:

- Environmental Abatement of Building 19 Roofing Elements

- Environmental Abatement of Asbestos and LBP elements within Building 19

Roof System Replacement

Roof demolition and removal of existing building roof system down to the concrete roof deck including the areas at the base of perimeter masonry parapet walls and any mechanical roof curbs and roof/parapet penetrations and scuppers. Roofing demolition will require coordination with the mechanical and electrical system contractor(s) in the removal of any mechanical systems and services presently on the existing roof. This will allow for the installation of a new insulated EPDM roofing system. Additionally, the roof replacement portion of the project will entail the limited repairs and replacement of masonry wall sections, repointing of limited masonry wall areas and the removal and replacement of limited deteriorated parapet wall coping stones. Where masonry repointing is necessary and required, the GC will employ all necessary silica dust control procedures and protocols.

Interior Demotion and Renovation Construction

Interior Demolition:  Removal of all interior drywall & ceiling systems as noted on the contract documents and specifications. All demolition work shall be coordinated with the appropriate mechanical, electrical, plumbing, and environmental abatement trades. Construction Phasing for this portion of the work will be coordinated with the project COR along with all Life Safety and Infection Controls procedures and protocols.

Interior Renovations: Construct new drywall partition systems and acoustical ceiling systems as noted on the contract drawings and specifications. All renovation work shall be coordinated with the appropriate mechanical, electrical, plumbing and environmental abatement trades. Construction Phasing for this portion of the work will be coordinated with the project COTR along with all Life Safety and Infection Controls procedures and protocols.

Electrical, HVAC, Plumbing Systems, Life Safety (Sprinkler and Fire Alarm Modifications)

Electrical: Electrical demolition work on this project will include but not be limited to the removal of existing electrical wired devices, lighting  fixtures, circuit panels,  etc.; installation of existing and new power and lighting including all conduits, conductors, junction boxes, hangers, attachments, etc. as required for a complete and working system.

Mechanical: Mechanical construction work on this project including relocation of existing steam trench piping systems and accessories, removal and modifications to existing heating and ventilation duct systems.

Plumbing:  The removal and capping or existing plumbing systems and the installation of all new plumbing system piping and components as indicated on the contract drawings and specifications.

Fire Alarm System and Sprinklers Modifications: Removal & relocation/upgrades of existing fire alarm system devices including conduits, conductors, devices, alarm interfaces, etc. as required for a complete and working fire alarm life safety system.  This work will entail the testing, adjusting, reprogramming and recertification of the fire alarm system.  Additionally, this portion of the project will entail the modification of the existing fire sprinkler system as noted in the contract documents and project specifications.

Contractor will be responsible to coordinate and schedule work to minimize construction duration and shall be expected to plan work typically during duty hours of the Medical Center, other than utility ties-ins or work required in the COR’s opinion to be performed during off duty hours. Maintain all access to and egress from the building at all times for facility’s fire protection requirements and to meet the requirements of regulatory codes, laws, etc.

Temporary Quarters

A temporary trailer will be provided that will house 2 firemen for the duration of the project. Utility connections will be made that provide heat and air conditioning to the premises.

Contract Completion shall be 300 Calendar Days from the Notice to Proceed.

At no additional cost to the Government, the Contractor shall allow the VA’s in-house personnel to investigate and perform repairs above the ceiling on the job site for a period of forty five (45) calendar days after the existing ceiling is demolished and removed and prior to the start of the new ceiling installation.  Repairs to be performed by the VA’s personnel include fire stopping improperly sealed penetrations through the walls and the slab above the ceiling level and removing items which may be attached to the sprinkler system.  During this period, the Contractor shall work on other contract work items which are located outside of the corridor space.  Contractor shall coordinate with the COR.

B. ITEM II, GENERAL CONSTRUCTION: DEDUCT ALTERNATE #1 – BASE BID minus

# The contractor is to perform all work in the Base Bid less the inclusion of new automatic transfer switch and new emergency distribution panel. Refer to electrical drawings ED 100 and EP 140

# The period of performance for Bid Deduct Alternate Item # 2 construction will still be 300 calendar days from Notice to Proceed (NTP).

1.4 SPECIFICATIONS AND DRAWINGS FOR CONTRACTOR

A.	Drawings and contract documents may be obtained from the website where the solicitation is posted.  Additional copies will be at Contractor's expense.

1.5 CONSTRUCTION SECURITY REQUIREMENTS

A.	Security Plan:

1.	The security plan defines both physical and administrative security procedures that will remain effective for the entire duration of the project.

B.	Security Procedures:

1.	General Contractor’s employees shall not enter the project site without appropriate VA ID badge.  They may also be subject to inspection of their personal effects when entering or leaving the project site.

2.	Before starting work, the General Contractor shall give the Contracting Officer (CO) and the Contracting Officer’s Representative (COR)two weeks notice of contractor personnel scheduled to be on site to ensure the employees have started the process to obtain VA ID badges.  This notice is separate from any notices required for utility shutdown described later in this section.

3.	No photography of VA premises is allowed without written permission of the Contracting Officer.

4.	VA reserves the right to close down or shut down the project site and order General Contractor’s employees off the premises in the event of a national emergency.  The General Contractor may return to the site only with the written approval of the Contracting Officer.

C.	Key Control:

1.	The General Contractor shall provide duplicate keys and lock combinations to the Contracting officers representative (COR) for the purpose of security inspections of every area of project including tool boxes and parked vehicles.

2.	The General Contractor shall machine and take any emergency action turn over all permanent lock cylinders to the VA locksmith for permanent installation. See Section 08 71 00, DOOR HARDWARE and coordinate.

D.	Document Control:

1.	Before starting any work, the General Contractor/Sub Contractors shall submit an electronic security memorandum describing the approach to following goals and maintaining confidentiality of “sensitive information”.

2.	The General Contractor is responsible for safekeeping of all drawings, project manual and other project information.  This information shall be shared only with those with a specific need to accomplish the project.

3.	Certain documents, sketches, videos or photographs and drawings may be marked “Law Enforcement Sensitive” or “Sensitive Unclassified”.  Secure such information in separate containers and limit the access to only those who will need it for the project.  Return the information to the Contracting Officer upon request.

4.	These security documents shall not be removed or transmitted from the project site without the written approval of Contracting Officer.

5.	All paper waste or electronic media such as CD’s and diskettes shall be shredded and destroyed in a manner acceptable to the VA.

6.	Notify Contracting Officer and Site Security Officer immediately when there is a loss or compromise of “sensitive information”.

7.	All electronic information shall be stored in specified location following VA standards and procedures using an Engineering Document Management Software (EDMS).

a.	Security, access and maintenance of all project drawings, both scanned and electronic shall be performed and tracked through the EDMS system.

b.	“Sensitive information” including drawings and other documents may be attached to e-mail provided all VA encryption procedures are followed.

E.	Motor Vehicle Restrictions

1.	Vehicle authorization request shall be required for any vehicle entering the site and such request shall be submitted 24 hours before the date and time of access.  Access shall be restricted to picking up and dropping off materials and supplies.

2.	A limited number of (2 to 5) permits shall be issued for General Contractor and its employees for parking in designated areas only.

1.6 OPERATIONS AND STORAGE AREAS

A.	The Contractor shall confine all operations (including storage of materials) on Government premises to areas authorized or approved by the Contracting Officer. The Contractor shall hold and save the Government, its officers and agents, free and harmless from liability of any nature occasioned by the Contractor's performance.

(FAR 52.236-10)

B.	Working space and space available for storing materials shall be as determined by the COR.

C.	Workmen are subject to rules of Medical Center applicable to their conduct.

D.	Execute work in such a manner as to interfere as little as possible with work being done by others. Keep roads clear of construction materials, debris, standing construction equipment and vehicles at all times.

E.	Execute work so as to interfere as little as possible with normal functioning of Medical Center as a whole, including operations of utility services, fire protection systems and any existing equipment, and with work being done by others.  Use of equipment and tools that transmit vibrations and noises through the building structure, are not permitted in buildings that are occupied, during construction, jointly by patients or medical personnel, and Contractor's personnel, except as permitted by COR where required by limited working space.

1.	Do not store materials and equipment in other than assigned areas.

2.	Schedule delivery of materials and equipment to immediate construction working areas within buildings in use by Department of Veterans Affairs in quantities sufficient for not more than two work days. Provide unobstructed access to Medical Center areas required to remain in operation.

F.	Utilities Services: Where necessary to cut existing pipes, electrical wires, conduits, cables, etc., of utility services, or of fire protection systems or communications systems (except telephone), they shall be cut and capped at suitable places where shown; or, in absence of such indication, where directed by COR.  All such actions shall be coordinated with the COR or Utility Company involved:

1.	Whenever it is required that a connection fee be paid to a public utility provider for new permanent service to the construction project, for such items as water, sewer, electricity, gas or steam, payment of such fee shall be the responsibility of the Government and not the Contractor.

G.	Building No. 19 will be not occupied during performance of work.

1.	Contractor shall take all measures and provide all material necessary for protecting existing equipment and property in affected areas of construction against dust and debris, so that equipment and affected areas to be used in the Medical Centers operations will not be hindered. Contractor shall permit access to Department of Veterans Affairs personnel and patients through other construction areas which serve as routes of access to such affected areas and equipment.  These routes whether access or egress shall be isolated from the construction area by temporary partitions and have walking surfaces, lighting. etc to facilitate patient and staff access.   Coordinate alteration work in areas occupied by Department of Veterans Affairs so that Medical Center operations will continue during the construction period.

H.	When a building and/or construction site is turned over to Contractor, Contractor shall accept entire responsibility including upkeep and maintenance therefore:

1.	Contractor shall maintain a minimum temperature of 4 degrees C (40 degrees F) at all times, except as otherwise specified.

2.	Contractor shall maintain in operating condition existing fire protection and alarm equipment. In connection with fire alarm equipment, Contractor shall make arrangements for pre-inspection of site with Fire Department or Company (Department of Veterans Affairs or municipal) whichever will be required to respond to an alarm from Contractor's employee or watchman.

I.	Utilities Services: Maintain existing utility services for Medical Center at all times. Provide temporary facilities, labor, materials, equipment, connections, and utilities to assure uninterrupted services. Where necessary to cut existing water, steam, gases, sewer or air pipes, or conduits, wires, cables, etc. of utility services or of fire protection systems and communications systems (including telephone), they shall be cut and capped at suitable places where shown; or, in absence of such indication, where directed by COR.

1.	No utility service such as water, gas, steam, sewers or electricity, or fire protection systems and communications systems may be interrupted without prior approval of COR.  Electrical work shall be accomplished with all affected circuits or equipment de-energized. When an electrical outage cannot be accomplished, work on any energized circuits or equipment shall not commence without a detailed work plan, the Medical Center Director’s prior knowledge and written approval.  Refer to specification Sections 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS, 27 05 11 REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS and 28 05 00, COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY for additional requirements.

2.	Contractor shall submit a request to interrupt any such services to COR, in writing, 7 days in advance of proposed interruption. Request shall state reason, date, exact time of, and approximate duration of such interruption.

3.	Contractor will be advised (in writing) of approval of request, or of which other date and/or time such interruption will cause least inconvenience to operations of Medical Center.  Interruption time approved by Medical Center may occur at other than Contractor's normal working hours.

4.	Major interruptions of any system must be requested, in writing, at least 15 calendar days prior to the desired time and shall be performed as directed by the COR.

5.	In case of a contract construction emergency, service will be interrupted on approval of COR.  Such approval will be confirmed in writing as soon as practical.

6.	Whenever it is required that a connection fee be paid to a public utility provider for new permanent service to the construction project, for such items as water, sewer, electricity, gas or steam, payment of such fee shall be the responsibility of the Government and not the Contractor.

J.	Abandoned Lines: All service lines such as wires, cables, conduits, ducts, pipes and the like, and their hangers or supports, which are to be abandoned but are not required to be entirely removed, shall be sealed, capped or plugged at the main, branch or panel they originate from. The lines shall not be capped in finished areas, but shall be removed and sealed, capped or plugged in ceilings, within furred spaces, in unfinished areas, or within walls or partitions; so that they are completely behind the finished surfaces.

K.	Coordinate the work for this contract with other construction operations as directed by COR. This includes the scheduling of traffic and the use of roadways, as specified in Article, USE OF ROADWAYS.

1.7 ALTERATIONS

A.	Survey: Before any work is started, the Contractor shall make a thorough survey with the COR of area of Building 19 in which alterations occur and areas which are anticipated routes of access, and furnish a report, signed by both to the Contracting Officer.  This report shall list by rooms and spaces:

1.	Existing condition and types of resilient flooring, doors, windows, walls and other surfaces not required to be altered throughout // affected areas of Building 4.

2.	Existence and conditions of items such as plumbing fixtures and accessories, electrical fixtures, equipment, venetian blinds, shades, etc., required by drawings to be either reused or relocated, or both.

3.	Shall note any discrepancies between drawings and existing conditions at site.

4.	Shall designate areas for working space, materials storage and routes of access to areas within buildings where alterations occur and which have been agreed upon by Contractor and COR.

B.	Any items required by drawings to be either reused or relocated or both, found during this survey to be nonexistent, or in opinion of COR to be in such condition that their use is impossible or impractical, shall be furnished and/or replaced by Contractor with new items in accordance with specifications which will be furnished by Government. Provided the contract work is changed by reason of this subparagraph B, the contract will be modified accordingly, under provisions of clause entitled "DIFFERING SITE CONDITIONS" (FAR 52.236-2) and "CHANGES" (FAR 52.243-4 and VAAR 852.236-88).

C.	Re-Survey: Thirty days before expected partial or final inspection date, the Contractor and COR together shall make a thorough re-survey of the areas of buildings involved. They shall furnish a report on conditions then existing, of resilient flooring, doors, windows, walls and other surfaces as compared with conditions of same as noted in first condition survey report:

1.	Re-survey report shall also list any damage caused by Contractor to such flooring and other surfaces, despite protection measures; and, will form basis for determining extent of repair work required of Contractor to restore damage caused by Contractor's workmen in executing work of this contract.

D.	Protection: Provide the following protective measures:

1.	Wherever existing roof surfaces are disturbed they shall be protected against water infiltration. In case of leaks, they shall be repaired immediately upon discovery.

2.	Temporary protection against damage for portions of existing structures and grounds where work is to be done, materials handled and equipment moved and/or relocated.

3.	Protection of interior of existing structures at all times, from damage, dust and weather inclemency. Wherever work is performed, floor surfaces that are to remain in place shall be adequately protected prior to starting work, and this protection shall be maintained intact until all work in the area is completed.

1.8 RESTORATION

A.	Remove, cut, alter, replace, patch and repair existing work as necessary to install new work. Except as otherwise shown or specified, do not cut, alter or remove any structural work, and do not disturb any ducts, plumbing, steam, gas, or electric work without approval of the COR.  Existing work to be altered or extended and that is found to be defective in any way, shall be reported to the COR before it is disturbed.  Materials and workmanship used in restoring work, shall conform in type and quality to that of original existing construction, except as otherwise shown or specified.

B.	Upon completion of contract, deliver work complete and undamaged. Existing work (walls, ceilings, partitions, floors, mechanical and electrical work, lawns, paving, roads, walks, etc.) disturbed or removed as a result of performing required new work, shall be patched, repaired, reinstalled, or replaced with new work, and refinished and left in as good condition as existed before commencing work.

C.	At Contractor's own expense, Contractor shall immediately restore to service and repair any damage caused by Contractor's workmen to existing piping and conduits, wires, cables, etc., of utility services or of fire protection systems and communications systems (including telephone) which are not scheduled for discontinuance or abandonment.

D.	Expense of repairs to such utilities and systems not shown on drawings or locations of which are unknown will be covered by adjustment to contract time and price in accordance with clause entitled "CHANGES" (FAR 52.243-4 and VAAR 852.236-88) and "DIFFERING SITE CONDITIONS" (FAR 52.236-2).

1.9 PHYSICAL DATA

A.	Data and information furnished or referred to below is for the Contractor's information. The Government shall not be responsible for any interpretation of or conclusion drawn from the data or information by the Contractor.

1.10 LAYOUT OF WORK

A.	The Contractor shall lay out the work from Government established base lines and bench marks, indicated on the drawings, and shall be responsible for all measurements in connection with the layout. The Contractor shall furnish, at Contractor's own expense, all stakes, templates, platforms, equipment, tools, materials, and labor required to lay out any part of the work. The Contractor shall be responsible for executing the work to the lines and grades that may be established or indicated by the Contracting Officer. The Contractor shall also be responsible for maintaining and preserving all stakes and other marks established by the Contracting Officer until authorized to remove them. If such marks are destroyed by the Contractor or through Contractor's negligence before their removal is authorized, the Contracting Officer may replace them and deduct the expense of the replacement from any amounts due or to become due to the Contractor.

(FAR 52.236-17)

B.	Establish and plainly mark center lines for each building and corner of column lines and/or addition to each existing building, and such other lines and grades that are reasonably necessary to properly assure that location, orientation, and elevations established are in accordance with lines and elevations shown on contract drawings.

1.11 AS-BUILT DRAWINGS

A.	The contractor shall maintain two full size sets of as-built drawings which will be kept current during construction of the project, to include all contract changes, modifications and clarifications.

B.	All variations shall be shown in the same general detail as used in the contract drawings. To insure compliance, as-built drawings shall be made available for the COR’s review, as often as requested.

C.	Contractor shall deliver two approved completed sets of as-built drawings in the electronic version (scanned PDF) to the COR within 15 calendar days after the acceptance of the project by the COR.

D.	Paragraphs A, B, & C shall also apply to all shop drawings.

1.13 TEMPORARY TOILETS

A.	Contractor may have for use of Contractor's workmen, such toilet accommodations as may be assigned to Contractor by Medical Center. Contractor shall keep such places clean and be responsible for any damage done thereto by Contractor's workmen. Failure to maintain satisfactory condition in toilets will deprive Contractor of the privilege to use such toilets.

1.14 AVAILABILITY AND USE OF UTILITY SERVICES

A.	The Government shall make all reasonably required amounts of utilities available to the Contractor from existing outlets and supplies.

B.	Heat: Furnish temporary heat necessary to prevent injury to work and materials through dampness and cold. Use of open salamanders or any temporary heating devices which may be fire hazards or may smoke and damage finished work, will not be permitted. Maintain minimum temperatures as specified for various materials:

1.	Obtain heat by connecting to Medical Center heating distribution system.

C.	Electricity (for Construction and Testing): Furnish all temporary electric services.

1.	Obtain electricity by connecting to the Medical Center electrical distribution system. The Contractor shall meter and pay for electricity required for electric cranes and hoisting devices, electrical welding devices and any electrical heating devices providing temporary heat. Electricity for all other uses is available at no cost to the Contractor.

D.	Water (for Construction and Testing): Furnish temporary water service.

1.	Obtain water by connecting to the Medical Center water distribution system. Provide reduced pressure backflow preventer at each connection as per code. Water is available at no cost to the Contractor.

2.	Maintain connections, pipe, fittings and fixtures and conserve water-use so none is wasted. Failure to stop leakage or other wastes will be cause for revocation (at COR discretion) of use of water from Medical Center's system.

1.15 TESTS

A.	As per specification section 23 05 93 the contractor shall provide a written testing and commissioning plan complete with component level, equipment level, sub-system level and system level breakdowns.  The plan will provide a schedule and a written sequence of what will be tested, how and what the expected outcome will be.  This document will be submitted for approval prior to commencing work.  The contractor shall document the results of the approved plan and submit for approval with the as built documentation.

B.	Pre-test mechanical and electrical equipment and systems and make corrections required for proper operation of such systems before requesting final tests. Final test will not be conducted unless pre-tested.

C.	Conduct final tests required in various sections of specifications in presence of an authorized representative of the Contracting Officer. Contractor shall furnish all labor, materials, equipment, instruments, and forms, to conduct and record such tests.

D.	Mechanical and electrical systems shall be balanced, controlled and coordinated. A system is defined as the entire system which must be coordinated to work together during normal operation to produce results for which the system is designed. For example, air conditioning supply air is only one part of entire system which provides comfort conditions for a building. Other related components are return air, exhaust air, steam, chilled water, refrigerant, hot water, controls and electricity, etc. Another example of a system which involves several components of different disciplines is a boiler installation. Efficient and acceptable boiler operation depends upon the coordination and proper operation of fuel, combustion air, controls, steam, feedwater, condensate and other related components.

E.	All related components as defined above shall be functioning when any system component is tested. Tests shall be completed within a reasonably period of time during which operating and environmental conditions remain reasonably constant and are typical of the design conditions.

F.	Individual test result of any component, where required, will only be accepted when submitted with the test results of related components and of the entire system.

1.16 INSTRUCTIONS

A.	Contractor shall furnish Maintenance and Operating manuals (hard copies and electronic) and verbal instructions when required by the various sections of the specifications and as hereinafter specified.

B.	Manuals: Maintenance and operating manuals and one compact disc (four hard copies and one electronic copy each) for each separate piece of equipment shall be delivered to the Resident Engineer // COR // coincidental with the delivery of the equipment to the job site. Manuals shall be complete, detailed guides for the maintenance and operation of equipment. They shall include complete information necessary for starting, adjusting, maintaining in continuous operation for long periods of time and dismantling and reassembling of the complete units and sub-assembly components. Manuals shall include an index covering all component parts clearly cross-referenced to diagrams and illustrations. Illustrations shall include "exploded" views showing and identifying each separate item. Emphasis shall be placed on the use of special tools and instruments. The function of each piece of equipment, component, accessory and control shall be clearly and thoroughly explained. All necessary precautions for the operation of the equipment and the reason for each precaution shall be clearly set forth. Manuals must reference the exact model, style and size of the piece of equipment and system being furnished. Manuals referencing equipment similar to but of a different model, style, and size than that furnished will not be accepted.

C.	Instructions: Contractor shall provide qualified, factory-trained manufacturers' representatives to give detailed training to assigned Department of Veterans Affairs personnel in the operation and complete maintenance for each piece of equipment. All such training will be at the job site. These requirements are more specifically detailed in the various technical sections. Instructions for different items of equipment that are component parts of a complete system, shall be given in an integrated, progressive manner. All instructors for every piece of component equipment in a system shall be available until instructions for all items included in the system have been completed. This is to assure proper instruction in the operation of inter-related systems. All instruction periods shall be at such times as scheduled by the COR and shall be considered concluded only when the COR is satisfied in regard to complete and thorough coverage. The contractor shall submit a course outline with associated material to the COR for review and approval prior to scheduling training to ensure the subject matter covers the expectations of the VA and the contractual requirements.  The Department of Veterans Affairs reserves the right to request the removal of, and substitution for, any instructor who, in the opinion of the COR, does not demonstrate sufficient qualifications in accordance with requirements for instructors above.

1.17 RELOCATED EQUIPMENT AND ITEMS

A.	Contractor shall disconnect, dismantle as necessary, remove and reinstall in new location, all existing equipment and items shown to be relocated by the Contractor.

B.	Perform relocation of such equipment or items at such times and in such a manner as directed by the COR.

C.	Suitably cap existing service lines, such as steam, condensate return, water, drain, gas, air, vacuum and/or electrical, at the main whenever such lines are disconnected from equipment to be relocated. Remove abandoned lines in finished areas and cap as specified herein before under paragraph "Abandoned Lines".

D.	Provide all mechanical and electrical service connections, fittings, fastenings and any other materials necessary for assembly and installation of relocated equipment; and leave such equipment in proper operating condition.

E.	Contractor shall employ services of an installation engineer, who is an authorized representative of the manufacturer of this equipment to supervise assembly and installation of existing equipment, required to be relocated.

F.	All service lines such as noted above for relocated equipment shall be in place at point of relocation ready for use before any existing equipment is disconnected. Make relocated existing equipment ready for operation or use immediately after reinstallation.

1.18 CONSTRUCTION SIGN

A.	Provide a Construction Sign where directed by the COR.  All wood members shall be of framing lumber. Cover sign frame with 0.7 mm (24 gage) galvanized sheet steel nailed securely around edges and on all bearings. Provide three 100 by 100 mm (4 inch by 4 inch) posts (or equivalent round posts) set 1200 mm (four feet) into ground. Set bottom of sign level at 900 mm (three feet) above ground and secure to posts with through bolts. Make posts full height of sign. Brace posts with 50 x 100 mm (two by four inch) material as directed.

B.	Paint all surfaces of sign and posts two coats of white gloss paint. Border and letters shall be of black gloss paint, except project title which shall be blue gloss paint.

C.	Maintain sign and remove it when directed by the COR.

D.	Detail Drawing of construction sign showing required legend and other characteristics of sign is attached hereto and made a part of this specification.

1.19 SAFETY SIGN

A.	Provide a Safety Sign where directed by COR.   Face of sign shall be 19 mm (3/4 inch) thick exterior grade plywood.  Provide two 100 mm by 100 mm (four by four inch) posts extending full height of sign and 900 mm (three feet) into ground. Set bottom of sign level at 1200 mm (four feet) above ground.

B.	Paint all surfaces of Safety Sign and posts with one prime coat and two coats of white gloss paint. Letters and design shall be painted with gloss paint of colors noted.

C.	Maintain sign and remove it when directed by COR.

D.	Standard Detail Drawing Number SD10000-02(Found on VA TIL) of safety sign showing required legend and other characteristics of sign is  attached hereto and is made a part of this specification.

E.	Post the number of accident free days on a daily basis.

1.20 HISTORIC PRESERVATION

Where the Contractor or any of the Contractor's employees, prior to, or during the construction work, are advised of or discover any possible archeological, historical and/or cultural resources, the Contractor shall immediately notify the COR verbally, and then with a written follow up.

- - - E N D - - -

SECTION 01 32 16.15
Project SCHEDULES

(Small Projects – Design/Bid/Build)

PART 1- GENERAL

1.1 DESCRIPTION:

A.	The Contractor shall develop a Critical Path Method(CPM) plan and schedule demonstrating fulfillment of the contract requirements (Project Schedule), and shall keep the Project Schedule up-to-date in accordance with the requirements of this section and shall utilize the plan for scheduling, coordinating and monitoring work under this contract (including all activities of subcontractors, equipment vendors and suppliers). Conventional Critical Path Method (CPM) technique shall be utilized to satisfy both time and cost applications.

1.2 CONTRACTOR'S REPRESENTATIVE:

A.	The Contractor shall designate an authorized representative responsible for the Project Schedule including preparation, review and progress reporting with and to the Contracting Officer's Representative (COR).

B.	The Contractor's representative shall have direct project control and complete authority to act on behalf of the Contractor in fulfilling the requirements of this specification section.

C.	The Contractor’s representative shall have the option of developing the project schedule within their organization or to engage the services of an outside consultant.  If an outside scheduling consultant is utilized, Section 1.3 of this specification will apply.

1.3 CONTRACTOR'S CONSULTANT:

A.	The Contractor shall submit a qualification proposal to the COR, within 10 days of bid acceptance. The qualification proposal shall include:

1.	The name and address of the proposed consultant.

2.	Information to show that the proposed consultant has the qualifications to meet the requirements specified in the preceding paragraph.

3.	A representative sample of prior construction projects, which the proposed consultant has performed complete project scheduling services. These representative samples shall be of similar size and scope.

B.	The Contracting Officer has the right to approve or disapprove the proposed consultant and will notify the Contractor of the VA decision within seven calendar days from receipt of the qualification proposal. In case of disapproval, the Contractor shall resubmit another consultant within 10 calendar days for renewed consideration. The Contractor shall have their scheduling consultant approved prior to submitting any schedule for approval.

1.4 COMPUTER PRODUCED SCHEDULES

A.	The contractor shall provide monthly, to the Department of Veterans Affairs (VA), all computer-produced time/cost schedules and reports generated from monthly project updates. This monthly computer service will include: three copies of up to five different reports (inclusive of all pages) available within the user defined reports of the scheduling software approved by the Contracting Officer; a hard copy listing of all project schedule changes, and associated data, made at the update and an electronic file of this data; and the resulting monthly updated schedule in PDM format.  These must be submitted with and substantively support the contractor’s monthly payment request and the signed look ahead report. The COR shall identify the five different report formats that the contractor shall provide.

B.	The contractor shall be responsible for the correctness and timeliness of the computer-produced reports. The Contractor shall also responsible for the accurate and timely submittal of the updated project schedule and all CPM data necessary to produce the computer reports and payment request that is specified.

C.	The VA will report errors in computer-produced reports to the Contractor’s representative within ten calendar days from receipt of reports. The Contractor shall reprocess the computer-produced reports and associated diskette(s), when requested by the Contracting Officer’s representative, to correct errors which affect the payment and schedule for the project.

1.5 THE COMPLETE PROJECT schedule SUBMITTAL

A.	Within 45 calendar days after receipt of Notice to Proceed, the Contractor shall submit for the Contracting Officer's review; three blue line copies of the interim schedule on sheets of paper 765 x 1070 mm (30 x 42 inches) and an electronic file in the previously approved CPM schedule program. The submittal shall also include three copies of a computer-produced activity/event ID schedule showing project duration; phase completion dates; and other data, including event cost. Each activity/event on the computer-produced schedule shall contain as a minimum, but not limited to, activity/event ID, activity/event description, duration, budget amount, early start date, early finish date, late start date, late finish date and total float. Work activity/event relationships shall be restricted to finish-to-start or start-to-start without lead or lag constraints. Activity/event date constraints, not required by the contract, will not be accepted unless submitted to and approved by the Contracting Officer. The contractor shall make a separate written detailed request to the Contracting Officer identifying these date constraints and secure the Contracting Officer’s written approval before incorporating them into the network diagram. The Contracting Officer’s separate approval of the Project Schedule shall not excuse the contractor of this requirement. Logic events (non-work) will be permitted where necessary to reflect proper logic among work events, but must have zero duration. The complete working schedule shall reflect the Contractor's approach to scheduling the complete project. The final Project Schedule in its original form shall contain no contract changes or delays which may have been incurred during the final network diagram development period and shall reflect the entire contract duration as defined in the bid documents.  These changes/delays shall be entered at the first update after the final Project Schedule has been approved. The Contractor should provide their requests for time and supporting time extension analysis for contract time as a result of contract changes/delays, after this update, and in accordance with Article, ADJUSTMENT OF CONTRACT COMPLETION.

B.	Within 30 calendar days after receipt of the complete project interim Project Schedule and the complete final Project Schedule, the Contracting Officer or his representative, will do one or both of the following:

1.	Notify the Contractor concerning his actions, opinions, and objections.

2.	A meeting with the Contractor at or near the job site for joint review, correction or adjustment of the proposed plan will be scheduled if required. Within 14 calendar days after the joint review, the Contractor shall revise and shall submit three blue line copies of the revised Project Schedule, three copies of the revised computer-produced activity/event ID schedule and a revised electronic file as specified by the Contracting Officer. The revised submission will be reviewed by the Contracting Officer and, if found to be as previously agreed upon, will be approved.

C.	The approved baseline schedule and the computer-produced schedule(s) generated there from shall constitute the approved baseline schedule until subsequently revised in accordance with the requirements of this section.

D.	The Complete Project Schedule shall contain approximately _100 to 200_work activities/events.

1.6 WORK ACTIVITY/EVENT COST DATA

A.	The Contractor shall cost load all work activities/events except procurement activities. The cumulative amount of all cost loaded work activities/events (including alternates) shall equal the total contract price. Prorate overhead, profit and general conditions on all work activities/events for the entire project length. The contractor shall generate from this information cash flow curves indicating graphically the total percentage of work activity/event dollar value scheduled to be in place on early finish, late finish. These cash flow curves will be used by the Contracting Officer to assist him in determining approval or disapproval of the cost loading. Negative work activity/event cost data will not be acceptable, except on VA issued contract changes.

B.	The Contractor shall cost load work activities/events for guarantee period services, test, balance and adjust various systems in accordance with the provisions in Article, FAR 52.232 – 5 (PAYMENT UNDER FIXED-PRICE CONSTRUCTION CONTRACTS) and VAAR 852.236 – 83 (PAYMENT UNDER FIXED-PRICE CONSTRUCTION CONTRACTS).

C.	In accordance with FAR 52.236 – 1 (PERFORMANCE OF WORK BY THE CONTRACTOR) and VAAR 852.236 – 72 (PERFORMANCE OF WORK BY THE CONTRACTOR), the Contractor shall submit, simultaneously with the cost per work activity/event of the construction schedule required by this Section, a responsibility code for all activities/events of the project for which the Contractor's forces will perform the work.

D.	The Contractor shall cost load work activities/events for all BID ITEMS including ASBESTOS ABATEMENT. The sum of each BID ITEM work shall equal the value of the bid item in the Contractors' bid.

1.7 project schedule REQUIREMENTS

A.	Show on the project schedule the sequence of work activities/events required for complete performance of all items of work. The Contractor Shall:

1.	Show activities/events as:

a.	Contractor's time required for submittal of shop drawings, templates, fabrication, delivery and similar pre-construction work.

b.	Contracting Officer's and Architect-Engineer's review and approval of shop drawings, equipment schedules, samples, template, or similar items.

c.	Interruption of VA Facilities utilities, delivery of Government furnished equipment, and rough-in drawings, project phasing and any other specification requirements.

d.	Test, balance and adjust various systems and pieces of equipment, maintenance and operation manuals, instructions and preventive maintenance tasks.

e.	VA inspection and acceptance activity/event with a minimum duration of five work days at the end of each phase and immediately preceding any VA move activity/event required by the contract phasing for that phase.

2.	Show not only the activities/events for actual construction work for each trade category of the project, but also trade relationships to indicate the movement of trades from one area, floor, or building, to another area, floor, or building, for at least five trades who are performing major work under this contract.

3.	Break up the work into activities/events of a duration no longer than 20 work days each or one reporting period, except as to non-construction activities/events (i.e., procurement of materials, delivery of equipment, concrete and asphalt curing) and any other activities/events for which the COR may approve the showing of a longer duration. The duration for VA approval of any required submittal, shop drawing, or other submittals will not be less than 20 work days.

4.	Describe work activities/events clearly, so the work is readily identifiable for assessment of completion. Activities/events labeled "start," "continue," or "completion," are not specific and will not be allowed. Lead and lag time activities will not be acceptable.

5.	The schedule shall be generally numbered in such a way to reflect either discipline, phase or location of the work.

B.	The Contractor shall submit the following supporting data in addition to the project schedule:

1.	The appropriate project calendar including working days and holidays.

2.	The planned number of shifts per day.

3.	The number of hours per shift.

Failure of the Contractor to include this data shall delay the review of the submittal until the Contracting Officer is in receipt of the missing data.

C.	To the extent that the Project Schedule or any revised Project Schedule shows anything not jointly agreed upon, it shall not be deemed to have been approved by the COR. Failure to include any element of work required for the performance of this contract shall not excuse the Contractor from completing all work required within any applicable completion date of each phase regardless of the COR’s approval of the Project Schedule.

D.	Compact Disk Requirements and CPM Activity/Event Record Specifications: Submit to the VA an electronic file(s) containing one file of the data required to produce a schedule, reflecting all the activities/events of the complete project schedule being submitted.

1.8 PAYMENT TO THE CONTRACTOR:

A.	Monthly, the contractor shall submit the AIA application and certificate for payment documents G702 & G703 reflecting updated schedule activities and cost data in accordance with the provisions of the following Article, PAYMENT AND PROGRESS REPORTING, as the basis upon which progress payments will be made pursuant to Article, FAR 52.232 – 5 (PAYMENT UNDER FIXED-PRICE CONSTRUCTION CONTRACTS) and VAAR 852.236 – 83 (PAYMENT UNDER FIXED-PRICE CONSTRUCTION CONTRACTS). The Contractor shall be entitled to a monthly progress payment upon approval of estimates as determined from the currently approved updated project schedule. Monthly payment requests shall include: a listing of all agreed upon project schedule changes and associated data; and an electronic file (s) of the resulting monthly updated schedule.

B.	Approval of the Contractor’s monthly Application for Payment shall be contingent, among other factors, on the submittal of a satisfactory monthly update of the project schedule.

1.9 PAYMENT AND PROGRESS REPORTING

A.	Monthly schedule update meetings will be held on dates mutually agreed to by the COR and the Contractor. Contractor and their CPM consultant (if applicable) shall attend all monthly schedule update meetings. The Contractor shall accurately update the Project Schedule and all other data required and provide this information to the COR three work days in advance of the schedule update meeting. Job progress will be reviewed to verify:

1.	Actual start and/or finish dates for updated/completed activities/events.

2.	Remaining duration for each activity/event started, or scheduled to start, but not completed.

3.	Logic, time and cost data for change orders, and supplemental agreements that are to be incorporated into the Project Schedule.

4. Changes in activity/event sequence and/or duration which have been made, pursuant to the provisions of following Article, ADJUSTMENT OF CONTRACT COMPLETION.

5.	Completion percentage for all completed and partially completed activities/events.

6.	Logic and duration revisions required by this section of the specifications.

7.	Activity/event duration and percent complete shall be updated independently.

B.	After completion of the joint review, the contractor shall generate an updated computer-produced calendar-dated schedule and supply the Contracting Officer’s representative with reports in accordance with the Article, COMPUTER PRODUCED SCHEDULES, specified.

C.	After completing the monthly schedule update, the contractor’s representative or scheduling consultant shall rerun all current period contract change(s) against the prior approved monthly project schedule. The analysis shall only include original workday durations and schedule logic agreed upon by the contractor and resident engineer for the contract change(s). When there is a disagreement on logic and/or durations, the Contractor shall use the schedule logic and/or durations provided and approved by the resident engineer. After each rerun update, the resulting electronic project schedule data file shall be appropriately identified and submitted to the VA in accordance to the requirements listed in articles 1.4 and 1.7. This electronic submission is separate from the regular monthly project schedule update requirements and shall be submitted to the resident engineer within fourteen (14) calendar days of completing the regular schedule update. Before inserting the contract changes durations, care must be taken to ensure that only the original durations will be used for the analysis, not the reported durations after progress.  In addition, once the final network diagram is approved, the contractor must recreate all manual progress payment updates on this approved network diagram and associated reruns for contract changes in each of these update periods as outlined above for regular update periods.  This will require detailed record keeping for each of the manual progress payment updates.

D.	Following approval of the CPM schedule, the VA, the General Contractor, its approved CPM Consultant, RE office representatives, and all subcontractors needed, as determined by the SRE, shall meet to discuss the monthly updated schedule. The main emphasis shall be to address work activities to avoid slippage of project schedule and to identify any necessary actions required to maintain project schedule during the reporting period. The Government representatives and the Contractor should conclude the meeting with a clear understanding of those work and administrative actions necessary to maintain project schedule status during the reporting period. This schedule coordination meeting will occur after each monthly project schedule update meeting utilizing the resulting schedule reports from that schedule update. If the project is behind schedule, discussions should include ways to prevent further slippage as well as ways to improve the project schedule status, when appropriate.

1.10 RESPONSIBILITY FOR COMPLETION

A.	If it becomes apparent from the current revised monthly progress schedule that phasing or contract completion dates will not be met, the Contractor shall execute some or all of the following remedial actions:

1.	Increase construction manpower in such quantities and crafts as necessary to eliminate the backlog of work.

2.	Increase the number of working hours per shift, shifts per working day, working days per week, the amount of construction equipment, or any combination of the foregoing to eliminate the backlog of work.

3.	Reschedule the work in conformance with the specification requirements.

B.	Prior to proceeding with any of the above actions, the Contractor shall notify and obtain approval from the COR for the proposed schedule changes. If such actions are approved, the representative schedule revisions shall be incorporated by the Contractor into the Project Schedule before the next update, at no additional cost to the Government.

1.11 CHANGES TO the SCHEDULE

A.	Within 30 calendar days after VA acceptance and approval of any updated project schedule, the Contractor shall submit a revised electronic file (s) and a list of any activity/event changes including predecessors and successors for any of the following reasons:

1.	Delay in completion of any activity/event or group of activities/events, which may be involved with contract changes, strikes, unusual weather, and other delays will not relieve the Contractor from the requirements specified unless the conditions are shown on the CPM as the direct cause for delaying the project beyond the acceptable limits.

2.	Delays in submittals, or deliveries, or work stoppage are encountered which make rescheduling of the work necessary.

3.	The schedule does not represent the actual prosecution and progress of the project.

4.	When there is, or has been, a substantial revision to the activity/event costs regardless of the cause for these revisions.

B.	CPM revisions made under this paragraph which affect the previously approved computer-produced schedules for Government furnished equipment, vacating of areas by the VA Facility, contract phase(s) and sub phase(s), utilities furnished by the Government to the Contractor, or any other previously contracted item, shall be furnished in writing to the Contracting Officer for approval.

C.	Contracting Officer's approval for the revised project schedule and all relevant data is contingent upon compliance with all other paragraphs of this section and any other previous agreements by the Contracting Officer or the VA representative.

D.	The cost of revisions to the project schedule resulting from contract changes will be included in the proposal for changes in work as specified in FAR 52.243 – 4 (Changes) and VAAR 852.236 – 88 (Changes – Supplemental), and will be based on the complexity of the revision or contract change, man hours expended in analyzing the change, and the total cost of the change.

E.	The cost of revisions to the Project Schedule not resulting from contract changes is the responsibility of the Contractor.

1.12 ADJUSTMENT OF CONTRACT COMPLETION

A.	The contract completion time will be adjusted only for causes specified in this contract. Request for an extension of the contract completion date by the Contractor shall be supported with a justification, CPM data and supporting evidence as the COR may deem necessary for determination as to whether or not the Contractor is entitled to an extension of time under the provisions of the contract. Submission of proof based on revised activity/event logic, durations (in work days) and costs is obligatory to any approvals. The schedule must clearly display that the Contractor has used, in full, all the float time available for the work involved in this request. The Contracting Officer's determination as to the total number of days of contract extension will be based upon the current computer-produced calendar-dated schedule for the time period in question and all other relevant information.

B.	Actual delays in activities/events which, according to the computer- produced calendar-dated schedule, do not affect the extended and predicted contract completion dates shown by the critical path in the network, will not be the basis for a change to the contract completion date. The Contracting Officer will within a reasonable time after receipt of such justification and supporting evidence, review the facts and advise the Contractor in writing of the Contracting Officer's decision.

C.	The Contractor shall submit each request for a change in the contract completion date to the Contracting Officer in accordance with the provisions specified under FAR 52.243 – 4 (Changes) and VAAR 852.236 – 88 (Changes – Supplemental). The Contractor shall include, as a part of each change order proposal, a sketch showing all CPM logic revisions, duration (in work days) changes, and cost changes, for work in question and its relationship to other activities on the approved network diagram.

D.	All delays due to non-work activities/events such as RFI’s, WEATHER, STRIKES, and similar non-work activities/events shall be analyzed on a month by month basis.

- - - E N D - - -

SECTION 01 33 23

SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES

# PART 1 – GENERAL

1.1 DESCRIPTION

- This specification defines the general requirements and procedures for submittals. A submittal is information submitted for VA review to establish compliance with the contract documents.

- Detailed submittal requirements are found in the technical sections of the contract specifications. The Contracting Officer may request submittals in addition to those specified when deemed necessary to adequately describe the work covered in the respective technical specifications at no additional cost to the government.

- VA approval of a submittal does not relieve the Contractor of the responsibility for any error which may exist. The Contractor is responsible for fully complying with all contract requirements and the satisfactory construction of all work, including the need to check, confirm, and coordinate the work of all subcontractors for the project.  Non-compliant material incorporated in the work will be removed and replaced at the Contractor’s expense.

1.2 DEFINITIONS

A.	Preconstruction Submittals:  Submittals which are required prior to issuing contract notice to proceed or starting construction.  For example, Certificates of insurance; Surety bonds; Site-specific safety plan; Construction progress schedule; Schedule of values; Submittal register; List of proposed subcontractors.

B.	Shop Drawings:  Drawings, diagrams, and schedules specifically prepared to illustrate some portion of the work. Drawings prepared by or for the Contractor to show how multiple systems and interdisciplinary work will be integrated and coordinated.

C.	Product Data: Catalog cuts, illustrations, schedules, diagrams, performance charts, instructions, and brochures, which describe and illustrate size, physical appearance, and other characteristics of materials, systems, or equipment for some portion of the work. Samples of warranty language when the contract requires extended product warranties.

- Samples: Physical examples of materials, equipment, or workmanship that illustrate functional and aesthetic characteristics of a material or product and establish standards by which the work can be judged.  Color samples from the manufacturer's standard line (or custom color samples if specified) to be used in selecting or approving colors for the project.  Field samples and mock-ups constructed to establish standards by which the ensuing work can be judged.

- Design Data: Calculations, mix designs, analyses, or other data pertaining to part of work.

- Test Reports: Report which includes findings of a test required to be performed by the Contractor on an actual portion of the work.  Report which includes finding of a test made at the job site or on sample taken from the job site, on portion of work during or after installation.

- Certificates: Document required of Contractor, or of a manufacturer, supplier, installer, or subcontractor through Contractor.  The purpose is to document procedures, acceptability of methods, or personnel qualifications for a portion of the work.

- Manufacturer's Instructions:  Pre-printed material describing installation of a product, system, or material, including special notices and MSDS concerning impedances, hazards, and safety precautions.

- Manufacturer's Field Reports: Documentation of the testing and verification actions taken by manufacturer's representative at the job site on a portion of the work, during or after installation, to confirm compliance with manufacturer's standards or instructions.  The documentation must indicate whether the material, product, or system has passed or failed the test.

- Operation and Maintenance Data: Manufacturer data that is required to operate, maintain, troubleshoot, and repair equipment, including manufacturer's help, parts list, and product line documentation.  This data shall be incorporated in an operations and maintenance manual.

- Closeout Submittals:  Documentation necessary to properly close out a construction contract.  For example, Record Drawings and as-built drawings. Also, submittal requirements necessary to properly close out a phase of construction on a multi-phase contract.

1.3 SUBMITTAL REGISTER

A.	The submittal register will list items of equipment and materials for which submittals are required by the specifications. This list may not be all inclusive and additional submittals may be required by the specifications.  The Contractor is not relieved from supplying submittals required by the contract documents but which have been omitted from the submittal register.

B.	The submittal register will serve as a scheduling document for submittals and will be used to control submittal actions throughout the contract period.

C.	The VA will provide the initial submittal register in electronic format. Thereafter, the Contractor shall track all submittals by maintaining a complete list, including completion of all data columns, including dates on which submittals are received and returned by the VA.

D.	The Contractor shall update the submittal register as submittal actions occur and maintain the submittal register at the project site until final acceptance of all work by Contracting Officer.

E.	The Contractor shall submit formal monthly updates to the submittal register in electronic format. Each monthly update shall document actual submission and approval dates for each submittal.

1.4 SUBMITTAL SCHEDULING

A.	Submittals are to be scheduled, submitted, reviewed, and approved prior to the acquisition of the material or equipment.

B.	Coordinate scheduling, sequencing, preparing, and processing of submittals with performance of work so that work will not be delayed by submittal processing.  Allow time for potential resubmittal.

C.	No delay costs or time extensions will be allowed for time lost in late submittals or resubmittals.

D.	All submittals are required to be approved prior to the start of the specified work activity.

1.5 SUBMITTAL PREPARATION

A.	Each submittal is to be complete and in sufficient detail to allow ready determination of compliance with contract requirements.

B.	Collect required data for each specific material, product, unit of work, or system into a single submittal. Prominently mark choices, options, and portions applicable to the submittal. Partial submittals will not be accepted for expedition of construction effort. Submittal will be returned without review if incomplete.

C.	If available product data is incomplete, provide Contractor-prepared documentation to supplement product data and satisfy submittal requirements.

D.	All irrelevant or unnecessary data shall be removed from the submittal to facilitate accuracy and timely processing. Submittals that contain the excessive amount of irrelevant or unnecessary data will be returned with review.

E.	Provide a transmittal form for each submittal with the following information:

- Project title, location and number.

- Construction contract number.

- Date of the drawings and revisions.

- Name, address, and telephone number of subcontractor, supplier, manufacturer, and any other subcontractor associated with the submittal.

- List paragraph number of the specification section and sheet number of the contract drawings by which the submittal is required.

- When a resubmission, add alphabetic suffix on submittal description.  For example, submittal 18 would become 18A, to indicate resubmission.

- Product identification and location in project.

F.	The Contractor is responsible for reviewing and certifying that all submittals are in compliance with contract requirements before submitting for VA review. Proposed deviations from the contract requirements are to be clearly identified. All deviations submitted must include a side by side comparison of item being proposed against item specified. Failure to point out deviations will result in the VA requiring removal and replacement of such work at the Contractor's expense.

G.	Stamp, sign, and date each submittal transmittal form indicating action taken.

H.	Stamp used by the Contractor on the submittal transmittal form to certify that the submittal meets contract requirements is to be similar to the following:

|	CONTRACTOR	|

|	|

|	(Firm Name)	|

|	|

|	|

|	|

|	Approved	|

|	|

|	|

|	Approved with corrections as noted on submittal data and/or	|

| attached sheets(s)	|

|	|

|	|

|	|

| SIGNATURE:		 |

|	|

| TITLE:		 |

|	|

| DATE:		 |

|	|

|	|

1.6 SUBMITTAL FORMAT AND TRANSMISSION

A.	Provide submittals in electronic format, with the exception of material samples.  Use PDF as the electronic format, unless otherwise specified or directed by the Contracting Officer.

B.	Compile the electronic submittal file as a single, complete document.  Name the electronic submittal file specifically according to its contents.

C.	Electronic files must be of sufficient quality that all information is legible.  Generate PDF files from original documents so that the text included in the PDF file is both searchable and can be copied.  If documents are scanned, Optical Character Resolution (OCR) routines are required.

D.	E-mail electronic submittal documents smaller than 5MB in size to e-mail addresses as directed by the Contracting Officer.

E.	Provide electronic documents over 5MB through an electronic FTP file sharing system.  Confirm that the electronic FTP file sharing system can be accessed from the VA computer network. The Contractor is responsible for setting up, providing, and maintaining the electronic FTP file sharing system for the construction contract period of performance.

F.	Provide hard copies of submittals when requested by the Contracting Officer.  Up to 3 additional hard copies of any submittal may be requested at the discretion of the Contracting Officer, at no additional cost to the VA.

1.7 SAMPLES

A.	Submit two sets of physical samples showing range of variation, for each required item.

B.	Where samples are specified for selection of color, finish, pattern, or texture, submit the full set of available choices for the material or product specified.

C.	When color, texture, or pattern is specified by naming a particular manufacturer and style, include one sample of that manufacturer and style, for comparison.

D.	Before submitting samples, the Contractor is to ensure that the materials or equipment will be available in quantities required in the project.  No change or substitution will be permitted after a sample has been approved.

E.	The VA reserves the right to disapprove any material or equipment which previously has proven unsatisfactory in service.

F.	Physical samples supplied maybe requested back for use in the project after reviewed and approved.

1.8 OPERATION AND MAINTENANCE DATA

A.	Submit data specified for a given item within 30 calendar days after the item is delivered to the contract site.

B.	In the event the Contractor fails to deliver O&M Data within the time limits specified, the Contracting Officer may withhold from progress payments 50 percent of the price of the item with which such O&M Data are applicable.

1.9 test reports

SRE may require specific test after work has been installed or completed which could require contractor to repair test area at no additional cost to contract.

1.10 VA REVIEW OF SUBMITTALS AND RFIs

A.	The VA will review all submittals for compliance with the technical requirements of the contract documents. The Architect-Engineer for this project will assist the VA in reviewing all submittals and determining contractual compliance.  Review will be only for conformance with the applicable codes, standards and contract requirements.

B.	Period of review for submittals begins when the VA COR receives submittal from the Contractor.

C.	Period of review for each resubmittal is the same as for initial submittal.

D.	VA review period is 15 working days for submittals.

E.	VA review period is 10 working days for RFIs.

F.	The VA will return submittals to the Contractor with the following notations:

- "Approved": authorizes the Contractor to proceed with the work covered.

- "Approved as noted": authorizes the Contractor to proceed with the work covered provided the Contractor incorporates the noted comments and makes the noted corrections.

- "Disapproved, revise and resubmit": indicates noncompliance with the contract requirements or that submittal is incomplete.  Resubmit with appropriate changes and corrections.  No work shall proceed for this item until resubmittal is approved.

- "Not reviewed": indicates submittal does not have evidence of being reviewed and approved by Contractor or is not complete.  A submittal marked "not reviewed" will be returned with an explanation of the reason it is not reviewed.  Resubmit submittals after taking appropriate action.

1.11 APPROVED SUBMITTALS

A.	The VA approval of submittals is not to be construed as a complete check, and indicates only that the general method of construction, materials, detailing, and other information are satisfactory.

B.	VA approval of a submittal does not relieve the Contractor of the responsibility for any error which may exist.  The Contractor is responsible for fully complying with all contract requirements and the satisfactory construction of all work, including the need to check, confirm, and coordinate the work of all subcontractors for the project.  Non-compliant material incorporated in the work will be removed and replaced at the Contractor’s expense.

C.	After submittals have been approved, no resubmittal for the purpose of substituting materials or equipment will be considered unless accompanied by an explanation of why a substitution is necessary.

D.	Retain a copy of all approved submittals at project site, including approved samples.

1.12 WITHHOLDING OF PAYMENT

Payment for materials incorporated in the work will not be made if required approvals have not been obtained.

- - - E N D - - -

SECTION 01 35 26
Safety REQUIREMENTS

TABLE OF CONTENTS

1.1	APPLICABLE PUBLICATIONS	3

1.2	DEFINITIONS	5

1.3	REGULATORY REQUIREMENTS	6

1.4	ACCIDENT PREVENTION PLAN (APP)	6

1.5	ACTIVITY HAZARD ANALYSES (AHAs)	12

1.6	PRECONSTRUCTION CONFERENCE	13

1.7	“SITE SAFETY AND HEALTH OFFICER” (SSHO) and “COMPETENT PERSON” (CP)		14

1.8	TRAINING	15

1.9	INSPECTIONS	16

1.10	ACCIDENTS, OSHA 300 LOGS, AND MAN-HOURS	17

1.11	PERSONAL PROTECTIVE EQUIPMENT (PPE)	18

1.12	INFECTION CONTROL	19

1.13	TUBERCULOSIS SCREENING	28

1.14	FIRE SAFETY	29

1.15	ELECTRICAL	33

1.16	FALL PROTECTION	34

1.17	SCAFFOLDS AND OTHER WORK PLATFORMS	35

1.18	EXCAVATION AND TRENCHES	36

1.19	CRANES	37

1.20	CONTROL OF HAZARDOUS ENERGY (LOCKOUT/TAGOUT)	37

1.21	CONFINED SPACE ENTRY	37

1.22	WELDING AND CUTTING	37

1.23	LADDERS	38

1.24	FLOOR & WALL OPENINGS	38

SECTION 01 35 26
Safety REQUIREMENTS

1.1 APPLICABLE PUBLICATIONS:

- Latest publications listed below form part of this Article to extent referenced. Publications are referenced in text by basic designations only.

- American Society of Safety Engineers (ASSE):

A10.1-2011	Pre-Project & Pre-Task Safety and Health Planning

A10.34-2012	Protection of the Public on or Adjacent to Construction Sites

A10.38-2013	Basic Elements of an Employer’s Program to Provide a Safe and Healthful Work Environment American National Standard Construction and Demolition Operations

- American Society for Testing and Materials (ASTM):

E84-2013	Surface Burning Characteristics of Building Materials

- The Facilities Guidelines Institute (FGI):

FGI Guidelines-2010Guidelines for Design and Construction of Healthcare Facilities

- National Fire Protection Association (NFPA):

10-2013	Standard for Portable Fire Extinguishers

30-2012	Flammable and Combustible Liquids Code

51B-2014	Standard for Fire Prevention During Welding, Cutting and Other Hot Work

70-2014	National Electrical Code

70B-2013	Recommended Practice for Electrical Equipment Maintenance

70E-2015 	Standard for Electrical Safety in the Workplace

99-2012	Health Care Facilities Code

241-2013	Standard for Safeguarding Construction, Alteration, and Demolition Operations

- The Joint Commission (TJC)

TJC Manual 	Comprehensive Accreditation and Certification Manual

- U.S. Nuclear Regulatory Commission

10 CFR 20 	Standards for Protection Against Radiation

- U.S. Occupational Safety and Health Administration (OSHA):

29 CFR 1904 	Reporting and Recording Injuries & Illnesses

29 CFR 1910 	Safety and Health Regulations for General Industry

29 CFR 1926 	Safety and Health Regulations for Construction Industry

CPL 2-0.124	Multi-Employer Citation Policy

- VHA Directive 2005-007

1.2 DEFINITIONS:

A.	Critical Lift. A lift with the hoisted load exceeding 75% of the crane’s maximum capacity; lifts made out of the view of the operator (blind picks); lifts involving two or more cranes; personnel being hoisted; and special hazards such as lifts over occupied facilities, loads lifted close to power-lines, and lifts in high winds or where other adverse environmental conditions exist; and any lift which the crane operator believes is critical.

B. OSHA “Competent Person” (CP). One who is capable of identifying existing and predictable hazards in the surroundings and working conditions which are unsanitary, hazardous or dangerous to employees, and who has the authorization to take prompt corrective measures to eliminate them (see 29 CFR 1926.32(f)).

C.	"Qualified Person" means one who, by possession of a recognized degree, certificate, or professional standing, or who by extensive knowledge, training and experience, has successfully demonstrated his ability to solve or resolve problems relating to the subject matter, the work, or the project.

D.	High Visibility Accident. Any mishap which may generate publicity or high visibility.

E. Accident/Incident Criticality Categories:

No impact – near miss incidents that should be investigated but are not required to be reported to the VA;

Minor incident/impact – incidents that require first aid or result in minor equipment damage (less than $5000). These incidents must be investigated but are not required to be reported to the VA;

Moderate incident/impact – Any work-related injury or illness that results in:

1.	Days away from work (any time lost after day of injury/illness onset);

2.	Restricted work;

3.	Transfer to another job;

4.	Medical treatment beyond first aid;

5.	Loss of consciousness;

6.	A significant injury or illness diagnosed by a physician or other licensed health care professional, even if it did not result in (1) through (5) above or,

7. any incident that leads to major equipment damage (greater than $5000).

These incidents must be investigated and are required to be reported to the VA;

Major incident/impact – Any mishap that leads to fatalities, hospitalizations, amputations, and losses of an eye as a result of contractors’ activities. Or any incident which leads to major property damage (greater than $20,000) and/or may generate publicity or high visibility. These incidents must be investigated and are required to be reported to the VA as soon as practical, but not later than 2 hours after the incident.

F.	Medical Treatment. Treatment administered by a physician or by registered professional personnel under the standing orders of a physician. Medical treatment does not include first aid treatment even through provided by a physician or registered personnel.

1.3 REGULATORY REQUIREMENTS:

A.	In addition to the detailed requirements included in the provisions of this contract, comply with 29 CFR 1926, comply with 29 CFR 1910 as incorporated by reference within 29 CFR 1926, comply with ASSE A10.34, and all applicable [federal, state, and local] laws, ordinances, criteria, rules and regulations. Submit matters of interpretation of standards for resolution before starting work. Where the requirements of this specification, applicable laws, criteria, ordinances, regulations, and referenced documents vary, the most stringent requirements govern except with specific approval and acceptance by the Contracting Officer Representative or Government Designated Authority.

1.4 ACCIDENT PREVENTION PLAN (APP):

- The APP (aka Construction Safety & Health Plan) shall interface with the Contractor's overall safety and health program. Include any portions of the Contractor's overall safety and health program referenced in the APP in the applicable APP element and ensure it is site-specific. The Government considers the Prime Contractor to be the "controlling authority" for all worksite safety and health of each subcontractor(s). Contractors are responsible for informing their subcontractors of the safety provisions under the terms of the contract and the penalties for noncompliance, coordinating the work to prevent one craft from interfering with or creating hazardous working conditions for other crafts, and inspecting subcontractor operations to ensure that accident prevention responsibilities are being carried out.

- The APP shall be prepared as follows:

- Written in English by a qualified person who is employed by the Prime Contractor articulating the specific work and hazards pertaining to the contract (model language can be found in ASSE A10.33).  Specifically articulating the safety requirements found within these VA contract safety specifications.

- Address both the Prime Contractors and the subcontractors work operations.

- State measures to be taken to control hazards associated with materials, services, or equipment provided by suppliers.

- Address all the elements/sub-elements and in order as follows:

- SIGNATURE SHEET. Title, signature, and phone number of the following:

1)	Plan preparer (Qualified Person such as corporate safety staff person or contracted Certified Safety Professional with construction safety experience);

2)	Plan approver (company/corporate officers authorized to obligate the company);

3)	Plan concurrence (e.g., Chief of Operations, Corporate Chief of Safety, Corporate Industrial Hygienist, project manager or superintendent, project safety professional). Provide concurrence of other applicable corporate and project personnel (Contractor).

b.	BACKGROUND INFORMATION. List the following:

1)	Contractor;

2)	Contract number;

3)	Project name;

4)	Brief project description, description of work to be performed, and location; phases of work anticipated (these will require an AHA).

c.	STATEMENT OF SAFETY AND HEALTH POLICY. Provide a copy of current corporate/company Safety and Health Policy Statement, detailing commitment to providing a safe and healthful workplace for all employees. The Contractor’s written safety program goals, objectives, and accident experience goals for this contract should be provided.

d.	RESPONSIBILITIES AND LINES OF AUTHORITIES. Provide the following:

1)	A statement of the employer’s ultimate responsibility for the implementation of his SOH program;

2)	Identification and accountability of personnel responsible for safety at both corporate and project level. Contracts specifically requiring safety or industrial hygiene personnel shall include a copy of their resumes.

3)	The names of Competent and/or Qualified Person(s) and proof of competency/qualification to meet specific OSHA Competent/Qualified Person(s) requirements must be attached.;

4)	Requirements that no work shall be performed unless a designated competent person is present on the job site;

5)	Requirements for pre-task Activity Hazard Analysis (AHAs);

6)	Lines of authority;

7)	Policies and procedures regarding noncompliance with safety requirements (to include disciplinary actions for violation of safety requirements) should be identified;

e.	SUBCONTRACTORS AND SUPPLIERS. If applicable, provide procedures for coordinating SOH activities with other employers on the job site:

1)	Identification of subcontractors and suppliers (if known);

2)	Safety responsibilities of subcontractors and suppliers.

f.	TRAINING.

1)	Site-specific SOH orientation training at the time of initial hire or assignment to the project for every employee before working on the project site is required.

2)	Mandatory training and certifications that are applicable to this project (e.g., explosive actuated tools, crane operator, rigger, crane signal person, fall protection, electrical lockout/NFPA 70E, machine/equipment lockout, confined space, etc…) and any requirements for periodic retraining/recertification are required.

3)	Procedures for ongoing safety and health training for supervisors and employees shall be established to address changes in site hazards/conditions.

4)	OSHA 10-hour training is required for all workers on site and the OSHA 30-hour training is required for Trade Competent Persons (CPs)

g.	SAFETY AND HEALTH INSPECTIONS.

1)	Specific assignment of responsibilities for a minimum daily job site safety and health inspection during periods of work activity: Who will conduct (e.g., “Site Safety and Health CP”), proof of inspector’s training/qualifications, when inspections will be conducted, procedures for documentation, deficiency tracking system, and follow-up procedures.

2)	Any external inspections/certifications that may be required (e.g., contracted CSP or CSHT)

h.	ACCIDENT/INCIDENT INVESTIGATION & REPORTING. The Contractor shall conduct mishap investigations of all Moderate and Major as well as all High Visibility Incidents. The APP shall include accident/incident investigation procedure and identify person(s) responsible to provide the following to the Contracting Officer Representative or Government Designated Authority:

1)	Exposure data (man-hours worked);

2)	Accident investigation reports;

3) Project site injury and illness logs.

i.	PLANS (PROGRAMS, PROCEDURES) REQUIRED. Based on a risk assessment of contracted activities and on mandatory OSHA compliance programs, the Contractor shall address all applicable occupational, patient, and public safety risks in site-specific compliance and accident prevention plans. These Plans shall include but are not be limited to procedures for addressing the risks associates with the following:

1)	Emergency response;

2)	Contingency for severe weather;

3)	Fire Prevention;

4)	Medical Support;

5)	Posting of emergency telephone numbers;

6)	Prevention of alcohol and drug abuse;

7)	Site sanitation(housekeeping, drinking water, toilets);

8)	Night operations and lighting;

9)	Hazard communication program;

10)	Welding/Cutting “Hot” work;

11)	Electrical Safe Work Practices (Electrical LOTO/NFPA 70E);

12)	General Electrical Safety;

13)	Hazardous energy control (Machine LOTO);

14)	Site-Specific Fall Protection & Prevention;

15)	Excavation/trenching;

16)	Asbestos abatement;

17)	Lead abatement;

18)	Crane Critical lift;

19)	Respiratory protection;

20)	Health hazard control program;

21)	Radiation Safety Program;

22)	Abrasive blasting;

23)	Heat/Cold Stress Monitoring;

24)	Crystalline Silica Monitoring (Assessment);

25)	Demolition plan (to include engineering survey);

26)	Formwork and shoring erection and removal;

27)	PreCast Concrete;

28) Public (Mandatory compliance with ANSI/ASSE A10.34-2012).

C.	Submit the APP to the Contracting Officer Representative or Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES fifteen [15] calendar days prior to the date of the preconstruction conference for acceptance. Work cannot proceed without an accepted APP.

D.	Once accepted by the Contracting Officer Representative or Government Designated Authority, the APP and attachments will be enforced as part of the contract. Disregarding the provisions of this contract or the accepted APP will be cause for stopping of work, at the discretion of the Contracting Officer in accordance with FAR Clause 52.236-13, Accident Prevention, until the matter has been rectified.

E.	Once work begins, changes to the accepted APP shall be made with the knowledge and concurrence of the Contracting Officer Representative. Should any severe hazard exposure, i.e. imminent danger, become evident, stop work in the area, secure the area, and develop a plan to remove the exposure and control the hazard. Notify the Contracting Officer within 24 hours of discovery. Eliminate/remove the hazard. In the interim, take all necessary action to restore and maintain safe working conditions in order to safeguard onsite personnel, visitors, the public and the environment.

1.5 ACTIVITY HAZARD ANALYSES (AHAs):

    - AHAs are also known as Job Hazard Analyses, Job Safety Analyses, and Activity Safety Analyses.  Before beginning each work activity involving a type of work presenting hazards not experienced in previous project operations or where a new work crew or sub-contractor is to perform the work, the Contractor(s) performing that work activity shall prepare an AHA (Example electronic AHA forms can be found on the US Army Corps of Engineers web site)

    - AHAs shall define the activities being performed and identify the work sequences, the specific anticipated hazards, site conditions, equipment, materials, and the control measures to be implemented to eliminate or reduce each hazard to an acceptable level of risk.

    - Work shall not begin until the AHA for the work activity has been accepted by the Contracting Officer Representative or Government Designated Authority and discussed with all engaged in the activity, including the Contractor, subcontractor(s), and Government on-site representatives at preparatory and initial control phase meetings.

1.	The names of the Competent/Qualified Person(s) required for a particular activity (for example, excavations, scaffolding, fall protection, other activities as specified by OSHA and/or other State and Local agencies) shall be identified and included in the AHA. Certification of their competency/qualification shall be submitted to the Government Designated Authority (GDA) for acceptance prior to the start of that work activity.

2.	The AHA shall be reviewed and modified as necessary to address changing site conditions, operations, or change of competent/qualified person(s).

a.	If more than one Competent/Qualified Person is used on the AHA activity, a list of names shall be submitted as an attachment to the AHA. Those listed must be Competent/Qualified for the type of work involved in the AHA and familiar with current site safety issues.

b.	If a new Competent/Qualified Person (not on the original list) is added, the list shall be updated (an administrative action not requiring an updated AHA). The new person shall acknowledge in writing that he or she has reviewed the AHA and is familiar with current site safety issues.

3.	Submit AHAs to the Contracting Officer Representative or Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES for review at least 15 calendar days prior to the start of each phase. Subsequent AHAs as shall be formatted as amendments to the APP. The analysis should be used during daily inspections to ensure the implementation and effectiveness of the activity's safety and health controls.

4.	The AHA list will be reviewed periodically (at least monthly) at the Contractor supervisory safety meeting and updated as necessary when procedures, scheduling, or hazards change.

5.	Develop the activity hazard analyses using the project schedule as the basis for the activities performed. All activities listed on the project schedule will require an AHA. The AHAs will be developed by the contractor, supplier, or subcontractor and provided to the prime contractor for review and approval and then submitted to the Contracting Officer Representative or Government Designated Authority.

1.6 PRECONSTRUCTION CONFERENCE:

A.	Contractor representatives who have a responsibility or significant role in implementation of the accident prevention program, as required by 29 CFR 1926.20(b)(1), on the project shall attend the preconstruction conference to gain a mutual understanding of its implementation. This includes the project superintendent, subcontractor superintendents, and any other assigned safety and health professionals.

B.	Discuss the details of the submitted APP to include incorporated plans, programs, procedures and a listing of anticipated AHAs that will be developed and implemented during the performance of the contract. This list of proposed AHAs will be reviewed at the conference and an agreement will be reached between the Contractor and the Contracting Officer's representative as to which phases will require an analysis. In addition, establish a schedule for the preparation, submittal, review, and acceptance of AHAs to preclude project delays.

C. Deficiencies in the submitted APP will be brought to the attention of the Contractor within 14 days of submittal, and the Contractor shall revise the plan to correct deficiencies and re-submit it for acceptance. Do not begin work until there is an accepted APP.SPEC WRITER NOTE: If the contract will involve (a) work of a long duration or hazardous nature, or (b) performance within a Government facility that on the advice of VA construction safety representatives involves hazardous operations that might endanger the safety of the public, patients and/or Government personnel or property, the SSHO and Superintendent and/or Quality Control Manager must be separate persons (See Section 1.7(C) for choice).

1.7 “SITE SAFETY AND HEALTH OFFICER” (SSHO) and “COMPETENT PERSON” (CP):

- The Prime Contractor shall designate a minimum of one SSHO at each project site that will be identified as the SSHO to administer the Contractor's safety program and government-accepted Accident Prevention Plan.  Each subcontractor shall designate a minimum of one CP in compliance with 29 CFR 1926.20 (b)(2) that will be identified as a CP to administer their individual safety programs.

- Further, all specialized Competent Persons for the work crews will be supplied by the respective contractor as required by 29 CFR 1926 (i.e. Asbestos, Electrical, Cranes, & Derricks, Demolition, Fall Protection, Fire Safety/Life Safety, Ladder, Rigging, Scaffolds, and Trenches/Excavations).

- These Competent Persons can have collateral duties as the subcontractor’s superintendent and/or work crew lead persons as well as fill more than one specialized CP role (i.e. Asbestos, Electrical, Cranes, & Derricks, Demolition, Fall Protection, Fire Safety/Life Safety, Ladder, Rigging, Scaffolds, and Trenches/Excavations).

- The SSHO or an equally-qualified Designated Representative/alternate will maintain a presence on the site during construction operations in accordance with FAR Clause 52.236-6: Superintendence by the Contractor.  CPs will maintain presence during their construction activities in accordance with above mentioned clause.  A listing of the designated SSHO and all known CPs shall be submitted prior to the start of work as part of the APP with the training documentation and/or AHA as listed in Section 1.8 below.

- The repeated presence of uncontrolled hazards during a contractor’s work operations will result in the designated CP as being deemed incompetent and result in the required removal of the employee in accordance with FAR Clause 52.236-5: Material and Workmanship, Paragraph (c).

1.8 TRAINING:

A.	The designated Prime Contractor SSHO must meet the requirements of all applicable OSHA standards and be capable (through training, experience, and qualifications) of ensuring that the requirements of 29 CFR 1926.16 and other appropriate Federal, State and local requirements are met for the project. As a minimum the SSHO must have completed the OSHA 30-hour Construction Safety class and have five (5) years of construction industry safety experience or three (3) years if he/she possesses a Certified Safety Professional (CSP) or certified Construction Safety and Health Technician (CSHT) certification or have a safety and health degree from an accredited university or college.

B.	All designated CPs shall have completed the OSHA 30-hour Construction Safety course within the past 5 years.

C.	In addition to the OSHA 30 Hour Construction Safety Course, all CPs with high hazard work operations such as operations involving asbestos, electrical, cranes, demolition, work at heights/fall protection, fire safety/life safety, ladder, rigging, scaffolds, and trenches/excavations shall have a specialized formal course in the hazard recognition & control associated with those high hazard work operations. Documented “repeat” deficiencies in the execution of safety requirements will require retaking the requisite formal course.

D.	All other construction workers shall have the OSHA 10-hour Construction Safety Outreach course and any necessary safety training to be able to identify hazards within their work environment.

E.	Submit training records associated with the above training requirements to the Contracting Officer Representative or Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES 15 calendar days prior to the date of the preconstruction conference for acceptance.

F.	Prior to any worker for the contractor or subcontractors beginning work, they shall undergo a safety briefing provided by the SSHO or his/her designated representative. As a minimum, this briefing shall include information on the site-specific hazards, construction limits, VAMC safety guidelines, means of egress, break areas, work hours, locations of restrooms, use of VAMC equipment, emergency procedures, accident reporting etc... Documentation shall be provided to the Resident Engineer that individuals have undergone contractor’s safety briefing.

G.	Ongoing safety training will be accomplished in the form of weekly documented safety meeting.

1.9 INSPECTIONS:

A.	The SSHO shall conduct frequent and regular safety inspections (daily) of the site and each of the subcontractors CPs shall conduct frequent and regular safety inspections (daily) of the their work operations as required by 29 CFR 1926.20(b)(2). Each week, the SSHO shall conduct a formal documented inspection of the entire construction areas with the subcontractors’ “Trade Safety and Health CPs” present in their work areas. Coordinate with, and report findings and corrective actions weekly to Contracting Officer Representative or Government Designated Authority.

1.10 ACCIDENTS, OSHA 300 LOGS, AND MAN-HOURS:

A.	The prime contractor shall establish and maintain an accident reporting, recordkeeping, and analysis system to track and analyze all injuries and illnesses, high visibility incidents, and accidental property damage (both government and contractor) that occur on site. Notify the Contracting Officer Representative or Government Designated Authority as soon as practical, but no more than four hours after any accident meeting the definition of a Moderate or Major incidents,  High Visibility Incidents, , or any weight handling and hoisting equipment accident. Within notification include contractor name; contract title; type of contract; name of activity, installation or location where accident occurred; date and time of accident; names of personnel injured; extent of property damage, if any; extent of injury, if known, and brief description of accident (to include type of construction equipment used, PPE used, etc.). Preserve the conditions and evidence on the accident site until the Contracting Officer Representative or Government Designated Authority determine whether a government investigation will be conducted.

B.	Conduct an accident investigation for all Minor, Moderate and Major incidents as defined in paragraph DEFINITIONS, and property damage accidents resulting in at least $20,000 in damages, to establish the root cause(s) of the accident. Complete the VA Form 2162 (or equivalent) , and provide the report to the Contracting Officer Representative or Government Designated Authority within 5 calendar days of the accident. The Contracting Officer Representative or Government Designated Authority will provide copies of any required or special forms.

C.	A summation of all man-hours worked by the contractor and associated sub-contractors for each month will be reported to the Contracting Officer Representative or Government Designated Authority monthly.

D.	A summation of all Minor, Moderate, and Major incidents experienced on site by the contractor and associated sub-contractors for each month will be provided to the Facility Safety or Contracting Officer Representative or Government Designated Authority monthly.  The contractor and associated sub-contractors’ OSHA 300 logs will be made available to the Contracting Officer Representative or Government Designated Authority as requested.

1.11 PERSONAL PROTECTIVE EQUIPMENT (PPE):

- PPE is governed in all areas by the nature of the work the employee is performing. For example, specific PPE required for performing work on electrical equipment is identified in NFPA 70E, Standard for Electrical Safety in the Workplace.

- Mandatory PPE includes:

1.	Hard Hats – unless written authorization is given by the Contracting Officer Representative or Government Designated Authority in circumstances of work operations that have limited potential for falling object hazards such as during finishing work or minor remodeling. With authorization to relax the requirement of hard hats, if a worker becomes exposed to an overhead falling object hazard, then hard hats would be required in accordance with the OSHA regulations.

2.	Safety glasses - unless written authorization is given by the Contracting Officer Representative or Government Designated Authority in circumstances of no eye hazards, appropriate safety glasses meeting the ANSI Z.87.1 standard must be worn by each person on site.

3.	Appropriate Safety Shoes – based on the hazards present, safety shoes meeting the requirements of ASTM F2413-11 shall be worn by each person on site unless written authorization is given by the Contracting Officer Representative or Government Designated Authority in circumstances of no foot hazards.

4.	Hearing protection - Use personal hearing protection at all times in designated noise hazardous areas or when performing noise hazardous tasks.

1.12 INFECTION CONTROL

- Infection Control is critical in all medical center facilities.  Interior construction activities causing disturbance of existing dust, or creating new dust, must be conducted within ventilation-controlled areas that minimize the flow of airborne particles into patient areas. Exterior construction activities causing disturbance of soil or creates dust in some other manner must be controlled.

- An AHA associated with infection control was performed by VA personnel in accordance with FGI Guidelines (i.e. Infection Control Risk Assessment (ICRA)).  The ICRA procedure found on the American Society for Healthcare Engineering (ASHE) website was utilized.

- Risk classifications of Class III or higher will require a permit before beginning any construction work. Infection Control permits will be issued by the COR.  The Infection Control Permits will be posted outside the appropriate construction area.  More than one permit may be issued for a construction project if the work is located in separate areas requiring separate classes. The primary project scope area for this project is: Class IV.  The required infection control precautions with each class are as follows:

Class IV requirements:

a.	During Construction Work:

1)	Obtain permit from the Contracting Officer Representative or Government Designated Authority

2)	Isolate HVAC system in area where work is being done to prevent contamination of duct system.

3)	Complete all critical barriers i.e. sheetrock, plywood, plastic, to seal area from non work area or implement control cube method (cart with plastic covering and sealed connection to work site with HEPA vacuum for vacuuming prior to exit) before construction begins.  Install construction barriers and ceiling protection carefully, outside of normal work hours.

4)	Maintain negative air pressure, 0.01 inches of water gauge, within work site utilizing HEPA equipped air filtration units and continuously monitored with a digital display, recording and alarm instrument, which must be calibrated on installation, maintained with periodic calibration and monitored by the contractor.5)	Seal holes, pipes, conduits, and punctures.

6)	Construct anteroom and require all personnel to pass through this room so they can be vacuumed using a HEPA vacuum cleaner before leaving work site or they can wear cloth or paper coveralls that are removed each time they leave work site.

7)	All personnel entering work site are required to wear shoe covers.  Shoe covers must be changed each time the worker exits the work area.

b.	Upon Completion:

1)	Do not remove barriers from work area until completed project is inspected by the Contracting Officer Representative or Government Designated Authority with thorough cleaning by the VA Environmental Services Dept.

2)	Remove construction barriers and ceiling protection carefully to minimize spreading of dirt and debris associated with construction, outside of normal work hours.

3)	Contain construction waste before transport in tightly covered containers.

4)	Cover transport receptacles or carts.  Tape covering unless solid lid.

5)	Vacuum work area with HEPA filtered vacuums.

6)	Wet mop area with cleaner/disinfectant.

7)	Upon completion, restore HVAC system where work was performed.

8)	Return permit to the Contracting Officer Representative or Government Designated Authority

- Barriers shall be erected as required based upon classification (Class III & IV requires barriers) and shall be constructed as follows:

1.	Class III and IV - closed door with masking tape applied over the frame and door is acceptable for projects that can be contained in a single room.

2.	Construction, demolition or reconstruction not capable of containment within a single room must have the following barriers erected and made presentable on hospital occupied side:

a.	Class III & IV (where dust control is the only hazard, and an agreement is reached with the Resident Engineer and Medical Center) - Airtight plastic barrier that extends from the floor to ceiling.  Seams must be sealed with duct tape to prevent dust and debris from escaping

b.	Class III & IV - Drywall barrier erected with joints covered or sealed to prevent dust and debris from escaping.

c.	Class III & IV - Seal all penetrations in existing barrier airtight

d.	Class III & IV - Barriers at penetration of ceiling envelopes, chases and ceiling spaces to stop movement air and debris

e.	Class IV only - Anteroom or double entrance openings that allow workers to remove protective clothing or vacuum off existing clothing

f.	Class III & IV - At elevators shafts or stairways within the field of construction, overlapping flap minimum of two feet wide of polyethylene enclosures for personnel access.

- Products and Materials:

1.	Sheet Plastic:  Fire retardant polystyrene, 6-mil thickness meeting local fire codes

2.	Barrier Doors: Self Closing One-hour fire-rated solid core wood in steel frame, painted

3.	Dust proof one-hour drywall

4.	High Efficiency Particulate Air-Equipped filtration machine rated at 95% capture of 0.3 microns including pollen, mold spores and dust particles.  HEPA filters should have ASHRAE 85 or other prefilter to extend the useful life of the HEPA. Provide both primary and secondary filtrations units.  Maintenance of equipment and replacement of the HEPA filters and other filters will be in accordance with manufacturer’s instructions.

5.	Exhaust Hoses: Heavy duty, flexible steel reinforced; Ventilation Blower Hose

6.	Adhesive Walk-off Mats: Provide minimum size mats of 24 inches x 36 inches

7.	Disinfectant: Hospital-approved disinfectant or equivalent product

8.	Portable Ceiling Access Module

- Before any construction on site begins, all contractor personnel involved in the construction or renovation activity shall be educated and trained in infection prevention measures established by the medical center.

- A dust control program will be establish and maintained as part of the contractor’s infection preventive measures in accordance with the FGI Guidelines for Design and Construction of Healthcare Facilities. Prior to start of work, prepare a plan detailing project-specific dust protection measures with associated product data, including periodic status reports, and submit to Engineer for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES.

- Medical center Infection Control personnel will monitor for airborne disease (e.g. aspergillosis) during construction. A baseline of conditions will be established by the medical center prior to the start of work and periodically during the construction stage to determine impact of construction activities on indoor air quality with safe thresholds established.

H.	In general, the following preventive measures shall be adopted during construction to keep down dust and prevent mold.

1.	Contractor shall verify that construction exhaust to exterior is not reintroduced to the medical center through intake vents, or building openings. HEPA filtration is required where the exhaust dust may reenter the medical center.

- Exhaust hoses shall be exhausted so that dust is not reintroduced to the medical center.

- Adhesive Walk-off/Carpet Walk-off Mats shall be used at all interior transitions from the construction area to occupied medical center area. These mats shall be changed as often as required to maintain clean work areas directly outside construction area at all times.

- Vacuum and wet mop all transition areas from construction to the occupied medical center at the end of each workday. Vacuum shall utilize HEPA filtration. Maintain surrounding area frequently. Remove debris as it is created. Transport these outside the construction area in containers with tightly fitting lids.

- Contractor shall remove all debris from the job site via a construction debris chute installed in an existing window opening.  Contractor shall carefully and temporarily remove existing window sashes and seal the opening with ½” thick fire rated plywood.  Opening for chute shall be sealed with fire rated plywood and fire rated caulk when no work is being performed.  Contractor shall re-install window sashes when project is completed.  The contractor shall not haul debris through patient-care areas without prior approval of the Resident Engineer and the Medical Center.  When approved, debris shall be hauled in enclosed dust proof containers or wrapped in plastic and sealed with duct tape. No sharp objects should be allowed to cut through the plastic. Wipe down the exterior of the containers with a damp rag to remove dust. All equipment, tools, material, etc. transported through occupied areas shall be made free from dust and moisture by vacuuming and wipe down.

- There shall be no standing water during construction. This includes water in equipment drip pans and open containers within the construction areas. All accidental spills must be cleaned up and dried within 12 hours. Remove and dispose of porous materials that remain damp for more than 72 hours.

- At completion, remove construction barriers and ceiling protection carefully, outside of normal work hours. Vacuum and clean all surfaces free of dust after the removal.

- Final Cleanup:

1.	Upon completion of project, or as work progresses, remove all construction debris from above ceiling, vertical shafts and utility chases that have been part of the construction.

2.	Perform HEPA vacuum cleaning of all surfaces in the construction area. This includes walls, ceilings, cabinets, furniture (built-in or free standing), partitions, flooring, etc.

3.	All new air ducts shall be cleaned prior to final inspection.

- Exterior Construction

1.	Contractor shall verify that dust will not be introduced into the medical center through intake vents, or building openings. HEPA filtration on intake vents is required where dust may be introduced.

2.	Dust created from disturbance of soil such as from vehicle movement will be wetted with use of a water truck as necessary

3.	All cutting, drilling, grinding, sanding, or disturbance of materials shall be accomplished with tools equipped with either local exhaust ventilation (i.e. vacuum systems) or wet suppression controls.

1.13 TUBERCULOSIS SCREENING

A.	Section Delited.

1.14 FIRE SAFETY

- Fire Safety Plan: Establish and maintain a site-specific fire protection program in accordance with 29 CFR 1926. Prior to start of work, prepare a plan detailing project-specific fire safety measures, including periodic status reports, and submit to Contracting Officer Representative or Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES. This plan may be an element of the Accident Prevention Plan.

- Site and Building Access: Maintain free and unobstructed access to facility emergency services and for fire, police and other emergency response forces in accordance with NFPA 241.

C.	Separate temporary facilities, such as trailers, storage sheds, and dumpsters, from existing buildings and new construction by distances in accordance with NFPA 241. For small facilities with less than 6 m (20 feet) exposing overall length, separate by 3m (10 feet).

D.	Temporary Construction Partitions:

1.	Install and maintain temporary construction partitions to provide smoke-tight separations between construction areas and adjoining areas. Construct partitions of gypsum board or treated plywood (flame spread rating of 25 or less in accordance with ASTM E84) on both sides of fire retardant treated wood or metal steel studs. Extend the partitions through suspended ceilings to floor slab deck or roof. Seal joints and penetrations. At door openings, install Class C, ¾ hour fire/smoke rated doors with self-closing devices.

2.	Install two-hour fire-rated temporary construction partitions as shown on drawings to maintain integrity of existing exit stair enclosures, exit passageways, fire-rated enclosures of hazardous areas, horizontal exits, smoke barriers, vertical shafts and openings enclosures.

3.	Close openings in smoke barriers and fire-rated construction to maintain fire ratings. Seal penetrations with listed through-penetration firestop materials in accordance with Section 07 84 00, FIRESTOPPING.

E.	Temporary Heating and Electrical: Install, use and maintain installations in accordance with 29 CFR 1926, NFPA 241 and NFPA 70.

F.	Means of Egress: Do not block exiting for occupied buildings, including paths from exits to roads. Minimize disruptions and coordinate with Contracting Officer Representative or Government Designated Authority.

G.	Egress Routes for Construction Workers: Maintain free and unobstructed egress. Inspect daily. Report findings and corrective actions weekly to Contracting Officer Representative or Government Designated Authority.

H.	Fire Extinguishers: Provide and maintain extinguishers in construction areas and temporary storage areas in accordance with 29 CFR 1926, NFPA 241 and NFPA 10.

I.	Flammable and Combustible Liquids: Store, dispense and use liquids in accordance with 29 CFR 1926, NFPA 241 and NFPA 30.

J.	Standpipes: Install and extend standpipes up with each floor in accordance with 29 CFR 1926 and NFPA 241.

K.	Existing Fire Protection: Do not impair automatic sprinklers, smoke and heat detection, and fire alarm systems, except for portions immediately under construction, and temporarily for connections. Provide fire watch for impairments more than 4 hours in a 24-hour period. Request interruptions in accordance with Article, OPERATIONS AND STORAGE AREAS, and coordinate with Contracting Officer Representative or Government Designated Authority. All existing or temporary fire protection systems (fire alarms, sprinklers) located in construction areas shall be tested as coordinated with the medical center. Parameters for the testing and results of any tests performed shall be recorded by the medical center and copies provided to the Resident Engineer.

L.	Smoke Detectors: Prevent accidental operation. Remove temporary covers at end of work operations each day. Coordinate with Contracting Officer Representative or Government Designated Authority.

M.	Hot Work: Perform and safeguard hot work operations in accordance with NFPA 241 and NFPA 51B. Coordinate with Facility Safety Office.  Obtain permits from Resident Engineer at least 24 hours in advance.

N.	Fire Hazard Prevention and Safety Inspections: Inspect entire construction areas weekly. Coordinate with, and report findings and corrective actions weekly to Contracting Officer Representative or Government Designated Authority.

O.	Smoking: Smoking is not allowed anywhere on campus.

P.	Dispose of waste and debris in accordance with NFPA 241. Remove from buildings daily.

Q.	If required, submit documentation to the COR that personnel have been trained in the fire safety aspects of working in areas with impaired structural or compartmentalization features.

1.15 ELECTRICAL

A.	All electrical work shall comply with NFPA 70 (NEC), NFPA 70B, NFPA 70E, 29 CFR Part 1910 Subpart J – General Environmental Controls, 29 CFR Part 1910 Subpart S – Electrical, and 29 CFR 1926 Subpart K in addition to other references required by contract.

B.	All qualified persons performing electrical work under this contract shall be licensed journeyman or master electricians. All apprentice electricians performing under this contract shall be deemed unqualified persons unless they are working under the immediate supervision of a licensed electrician or master electrician.

C.	All electrical work will be accomplished de-energized and in the Electrically Safe Work Condition (refer to NFPA 70E for Work Involving Electrical Hazards, including Exemptions to Work Permit).  Any Contractor, subcontractor or temporary worker who fails to fully comply with this requirement is subject to immediate termination in accordance with FAR clause 52.236-5(c).  Only in rare circumstance where achieving an electrically safe work condition prior to beginning work would increase or cause additional hazards, or is infeasible due to equipment design or operational limitations is energized work permitted. The Contracting Officer Representative or Government Designated Authority with approval of the Medical Center Director will make the determination if the circumstances would meet the exception outlined above. An AHA and permit specific to energized work activities will be developed, reviewed, and accepted by the VA prior to the start of that activity.

1.	Development of a Hazardous Electrical Energy Control Procedure is required prior to de-energization. A single Simple Lockout/Tagout Procedure for multiple work operations can only be used for work involving qualified person(s) de-energizing one set of conductors or circuit part source. Task specific Complex Lockout/Tagout Procedures are required at all other times.

2.	Verification of the absence of voltage after de-energization and lockout/tagout is considered “energized electrical work” (live work) under NFPA  70E, and shall only be performed by qualified persons wearing appropriate shock protective (voltage rated) gloves and arc rate personal protective clothing and equipment, using Underwriters Laboratories (UL) tested and appropriately rated contact electrical testing instruments or equipment appropriate for the environment in which they will be used.

3.	Personal Protective Equipment (PPE) and electrical testing instruments will be readily available for inspection by the Contracting Officer Representative or Government Designated Authority.

    - Before beginning any electrical work, an Activity Hazard Analysis (AHA) will be conducted to include Shock Hazard and Arc Flash Hazard analyses (NFPA Tables can be used only as a last alterative and it is strongly suggested a full Arc Flash Hazard Analyses be conducted).  Work shall not begin until the AHA for the work activity and permit for energized work has been reviewed and accepted by the Contracting Officer Representative or Government Designated Authority and discussed with all engaged in the activity, including the Contractor, subcontractor(s), and Government on-site representatives at preparatory and initial control phase meetings.

    - Ground-fault circuit interrupters. GFCI protection shall be provided where an employee is operating or using cord- and plug-connected tools related to construction activity supplied by 125-volt, 15-, 20-, or 30- ampere circuits. Where employees operate or use equipment supplied by greater than 125-volt, 15-, 20-, or 30- ampere circuits, GFCI protection or an assured equipment grounding conductor program shall be implemented in accordance with NFPA 70E - 2015, Chapter 1, Article 110.4(C)(2)..

1.16 FALL PROTECTION

A.	The fall protection (FP) threshold height requirement is 6 ft (1.8 m) for ALL WORK, unless specified differently or the OSHA 29 CFR 1926 requirements are more stringent, to include steel erection activities, systems-engineered activities (prefabricated) metal buildings, residential (wood) construction and scaffolding work.

1.	The use of a Safety Monitoring System (SMS) as a fall protection method is prohibited.

2.	The use of Controlled Access Zone (CAZ) as a fall protection method is prohibited.

3.	A Warning Line System (WLS) may ONLY be used on floors or flat or low-sloped roofs (between 0 - 18.4 degrees or 4:12 slope) and shall be erected around all sides of the work area (See 29 CFR 1926.502(f) for construction of WLS requirements).  Working within the WLS does not require FP. No worker shall be allowed in the area between the roof or floor edge and the WLS without FP. FP is required when working outside the WLS.

4.	Fall protection while using a ladder will be governed by the OSHA requirements.

1.17 SCAFFOLDS AND OTHER WORK PLATFORMS

A.	All scaffolds and other work platforms construction activities shall comply with 29 CFR 1926 Subpart L.

B.	The fall protection (FP) threshold height requirement is 6 ft (1.8 m) as stated in Section 1.16.

C.	The following hierarchy and prohibitions shall be followed in selecting appropriate work platforms.

1.	Scaffolds, platforms, or temporary floors shall be provided for all work except that can be performed safely from the ground or similar footing.

2.	Ladders less than 20 feet may be used as work platforms only when use of small hand tools or handling of light material is involved.

3.	Ladder jacks, lean-to, and prop-scaffolds are prohibited.

4.	Emergency descent devices shall not be used as working platforms.

D.	Contractors shall use a scaffold tagging system in which all scaffolds are tagged by the Competent Person. Tags shall be color-coded: green indicates the scaffold has been inspected and is safe to use; red indicates the scaffold is unsafe to use. Tags shall be readily visible, made of materials that will withstand the environment in which they are used, be legible and shall include:

1.	The Competent Person’s name and signature;

2.	Dates of initial and last inspections.

E.	Mast Climbing work platforms: When access ladders, including masts designed as ladders, exceed 20 ft (6 m) in height, positive fall protection shall be used.

1.18 EXCAVATION AND TRENCHES

A.	All excavation and trenching work shall comply with 29 CFR 1926 Subpart P.  Excavations less than 5 feet in depth require evaluation by the contractor’s “Competent Person” (CP) for determination of the necessity of an excavation protective system where kneeing, laying in, or stooping within the excavation is required.

B.	All excavations and trenches 15 inches in depth or greater shall require a written trenching and excavation permit (NOTE – some States and other local jurisdictions require separate state/jurisdiction-issued excavation permits).  The permit shall have two sections, one section will be completed prior to digging or drilling and the other will be completed prior to personnel entering the excavations greater than 5 feet in depth.  Each section of the permit shall be provided to Facility Safety and/or other Government Designated Authority prior to proceeding with digging or drilling and prior to proceeding with entering the excavation.  After completion of the work and prior to opening a new section of an excavation, the permit shall be closed out and provided to the Resident Engineer and/or other Government Designated Authority.  The permit shall be maintained onsite and the first section of the permit shall include the following:

1.	Estimated start time & stop time2.	Specific location and nature of the work.

3.	Indication of the contractor’s “Competent Person” (CP) in excavation safety with qualifications and signature.  Formal course in excavation safety is required by the contractor’s CP.

4.	Indication of whether soil or concrete removal to an offsite location is necessary.

5.	Indication of whether soil samples are required to determined soil contamination.

6. Indication of coordination with local authority (i.e. “One Call”) or contractor’s effort to determine utility location with search and survey equipment.

7. Indication of review of site drawings for proximity of utilities to digging/drilling.

The second section of the permit for excavations greater than five feet in depth shall include the following:

1.	Determination of OSHA classification of soil.  Soil samples will be from freshly dug soil with samples taken from different soil type layers as necessary and placed at a safe distance from the excavation by the excavating equipment. A pocket penetrometer will be utilized in determination of the unconfined compression strength of the soil for comparison against OSHA table (Less than 0.5 Tons/FT2 – Type C, 0.5 Tons/FT2 to 1.5 Tons/FT2 – Type B, greater than 1.5 Tons/FT2 – Type A without condition to reduce to Type B).

2.	Indication of selected protective system (sloping/benching, shoring, shielding).  When soil classification is identified as “Type A” or “Solid Rock”, only shoring or shielding or Professional Engineer designed systems can be used for protection.  A Sloping/Benching system may only be used when classifying the soil as Type B or Type C.  Refer to Appendix B of 29 CFR 1926, Subpart P for further information on protective systems designs.

3.	Indication of the spoil pile being stored at least 2 feet from the edge of the excavation and safe access being provided within 25 feet of the workers.

4.	Indication of assessment for a potential toxic, explosive, or oxygen deficient atmosphere where oxygen deficiency (atmospheres containing less than 19.5 percent oxygen) or a hazardous atmosphere exists or could reasonably be expected to exist.  Internal combustion engine equipment is not allowed in an excavation without providing force air ventilation to lower the concentration to below OSHA PELs, providing sufficient oxygen levels, and atmospheric testing as necessary to ensure safe levels are maintained.

C.	As required by OSHA 29 CFR 1926.651(b)(1), the estimated location of utility installations, such as sewer, telephone, fuel, electric, water lines, or any other underground installations that reasonably may be expected to be encountered during excavation work, shall be determined prior to opening an excavation.

1.	The planned dig site will be outlined/marked in white prior to locating the utilities.

2.	Used of the American Public Works Association Uniform Color Code is required for the marking of the proposed excavation and located utilities.

3.	811 will be called two business days before digging on all local or State lands and public Right-of Ways.

4.	Digging will not commence until all known utilities are marked.

5.	Utility markings will be maintained

D.	Excavations will be hand dug or excavated by other similar safe and acceptable means as excavation operations approach within 3 to 5 feet of identified underground utilities.  Exploratory bar or other detection equipment will be utilized as necessary to further identify the location of underground utilities.

E.	Excavations greater than 20 feet in depth require a Professional Engineer designed excavation protective system.

1.19 CRANES

A.	All crane work shall comply with 29 CFR 1926 Subpart CC.

B.	Prior to operating a crane, the operator must be licensed, qualified or certified to operate the crane.  Thus, all the provisions contained with Subpart CC are effective and there is no “Phase In” date.

C.	A detailed lift plan for all lifts shall be submitted to Facility Safety and/or other Government Designated Authority 14 days prior to the scheduled lift complete with route for truck carrying load, crane load analysis, siting of crane and path of swing and all other elements of a critical lift plan where the lift meets the definition of a critical lift. Critical lifts require a more comprehensive lift plan to minimize the potential of crane failure and/or catastrophic loss. The plan must be reviewed and accepted by the General Contractor before being submitted to the VA for review. The lift will not be allowed to proceed without prior acceptance of this document.

D.	Crane operators shall not carry loads

1.	over the general public or VAMC personnel

2.	over any occupied building unless

a.	the top two floors are vacated

b.	or overhead protection with a design live load of 300 psf is provided

1.20 CONTROL OF HAZARDOUS ENERGY (LOCKOUT/TAGOUT)

A.	All installation, maintenance, and servicing of equipment or machinery shall comply with 29 CFR 1910.147 except for specifically referenced operations in 29 CFR 1926 such as concrete & masonry equipment [1926.702(j)], heavy machinery & equipment [1926.600(a)(3)(i)], and process safety management of highly hazardous chemicals (1926.64).  Control of hazardous electrical energy during the installation, maintenance, or servicing of electrical equipment shall comply with Section 1.15 to include NFPA 70E and other VA specific requirements discussed in the section.

1.21 CONFINED SPACE ENTRY

A.	All confined space entry shall comply with 29 CFR 1926, Subpart AA except for specifically referenced operations in 29 CFR 1926 such as excavations/trenches [1926.651(g)].

B.	A site-specific Confined Space Entry Plan (including permitting process) shall be developed and submitted to Facility Safety and/or other Government Designated Authority.

1.22 WELDING AND CUTTING

As specified in section 1.14, Hot Work: Perform and safeguard hot work operations in accordance with NFPA 241 and NFPA 51B. Coordinate with Facility Safety and/or other Government Designated Authority.  Obtain permits from Facility Safety and/or other Government Designated Authority at least 24 hours in advance. Designate contractor's responsible project-site fire prevention program manager to permit hot work.

1.23 LADDERS

A.	All Ladder use shall comply with 29 CFR 1926 Subpart X.

B.	All portable ladders shall be of sufficient length and shall be placed so that workers will not stretch or assume a hazardous position.

C.	Manufacturer safety labels shall be in place on ladders

D.	Step Ladders shall not be used in the closed position

E.	Top steps or cap of step ladders shall not be used as a step

    - Portable ladders, used as temporary access, shall extend at least 3 ft (0.9 m) above the upper landing surface.

1.	When a 3 ft (0.9-m) extension is not possible, a grasping device (such as a grab rail) shall be provided to assist workers in mounting and dismounting the ladder.

2.	In no case shall the length of the ladder be such that ladder deflection under a load would, by itself, cause the ladder to slip from its support.

G.	Ladders shall be inspected for visible defects on a daily basis and after any occurrence that could affect their safe use. Broken or damaged ladders shall be immediately tagged "DO NOT USE," or with similar wording, and withdrawn from service until restored to a condition meeting their original design.

1.24 FLOOR & WALL OPENINGS

A.	All floor and wall openings shall comply with 29 CFR 1926 Subpart M.

B.	Floor and roof holes/openings are any that measure over 2 in (51 mm) in any direction of a walking/working surface which persons may trip or fall into or where objects may fall to the level below. See 21.F for covering and labeling requirements.   Skylights located in floors or roofs are considered floor or roof hole/openings.

C.	All floor, roof openings or hole into which a person can accidentally walk or fall through shall be guarded either by a railing system with toeboards along all exposed sides or a load-bearing cover. When the cover is not in place, the opening or hole shall be protected by a removable guardrail system or shall be attended when the guarding system has been removed, or other fall protection system.

1.	Covers shall be capable of supporting, without failure, at least twice the weight of the worker, equipment and material combined.

2.	Covers shall be secured when installed, clearly marked with the word “HOLE”, “COVER” or “Danger, Roof Opening-Do Not Remove” or color-coded or equivalent methods (e.g., red or orange “X”). Workers must be made aware of the meaning for color coding and equivalent methods.

3.	Roofing material, such as roofing membrane, insulation or felts, covering or partly covering openings or holes, shall be immediately cut out. No hole or opening shall be left unattended unless covered.

4.	Non-load-bearing skylights shall be guarded by a load-bearing skylight screen, cover, or railing system along all exposed sides.

5.	Workers are prohibited from standing/walking on skylights.

- - - E N D - - -

SECTION 01 42 19
REFERENCE STANDARDS

PART 1 - GENERAL

1.1 DESCRIPTION

This section specifies the availability and source of references and standards specified in the project manual under paragraphs APPLICABLE PUBLICATIONS and/or shown on the drawings.

1.2 AVAILABILITY OF SPECIFICATIONS LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM DESCRIPTIONS FPMR PART 101-29 (FAR 52.211-1) (AUG 1998)

A.	The GSA Index of Federal Specifications, Standards and Commercial Item Descriptions, FPMR Part 101-29 and copies of specifications, standards, and commercial item descriptions cited in the solicitation may be obtained for a fee by submitting a request to – GSA Federal Supply Service, Specifications Section, Suite 8100, 470 East L’Enfant Plaza, SW, Washington, DC 20407, Telephone (202) 619-8925, Facsimile (202) 619-8978.

B.	If the General Services Administration, Department of Agriculture, or Department of Veterans Affairs issued this solicitation, a single copy of specifications, standards, and commercial item descriptions cited in this solicitation may be obtained free of charge by submitting a request to the addressee in paragraph (a) of this provision. Additional copies will be issued for a fee.

1.3 AVAILABILITY FOR EXAMINATION OF SPECIFICATIONS NOT LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM descriptions (FAR 52.211-4) (JUN 1988)

The specifications and standards cited in this solicitation can be examined at the following location:

DEPARMENT OF VETERANS AFFAIRS
Office of Construction & Facilities Management
Facilities Quality Service (00CFM1A)
425 Eye Street N.W, (sixth floor)
Washington, DC 20001
Telephone Numbers: (202) 632-5249 or (202) 632-5178
Between 9:00 AM - 3:00 PM

1.4 AVAILABILITY OF SPECIFICATIONS NOT LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM DESCRIPTIONS (FAR 52.211-3) (JUN 1988)

The specifications cited in this solicitation may be obtained from the associations or organizations listed below.

AA	Aluminum Association Inc.
http://www.aluminum.org

AABC	Associated Air Balance Council
https://www.aabc.com

AAMA	American Architectural Manufacturer's Association
http://www.aamanet.org

AASHTO	American Association of State Highway and Transportation Officials
http://www.aashto.org

AATCC	American Association of Textile Chemists and Colorists
http://www.aatcc.org

ACGIH	American Conference of Governmental Industrial Hygienists
http://www.acgih.org

ACI	American Concrete Institute
http://www.aci-int.net

ACPA	American Concrete Pipe Association
http://www.concrete-pipe.org

ACPPA	American Concrete Pressure Pipe Association
http://www.acppa.org

ADC	Air Diffusion Council
http://flexibleduct.org

AGA	American Gas Association
http://www.aga.org

AGC	Associated General Contractors of America
http://www.agc.org

AGMA	American Gear Manufacturers Association, Inc.
http://www.agma.org

AH 	American Hort

https://www.americanhort.org

AHAM	Association of Home Appliance Manufacturers
http://www.aham.org

AIA	American Institute of Architects

http://www.aia.org

AISC	American Institute of Steel Construction
http://www.aisc.org

AISI	American Iron and Steel Institute
http://www.steel.org

AITC	American Institute of Timber Construction
https://aitc-glulam.org

AMCA	Air Movement and Control Association, Inc.
http://www.amca.org

ANSI	American National Standards Institute, Inc.
http://www.ansi.org

APA	The Engineered Wood Association
http://www.apawood.org

ARI	Air-Conditioning and Refrigeration Institute
http://www.ari.org

ARPM	Association for Rubber Product Manufacturers

https://arpm.com

ASABE	American Society of Agricultural and Biological Engineers
https://www.asabe.org

ASCE	American Society of Civil Engineers
http://www.asce.org

ASHRAE	American Society of Heating, Refrigerating, and
Air-Conditioning Engineers
http://www.ashrae.org

ASME	American Society of Mechanical Engineers
http://www.asme.org

ASSE	American Society of Sanitary Engineering International
http://www.asse-plumbing.org

ASTM	American Society for Testing and Materials International
http://www.astm.org

AWI	Architectural Woodwork Institute
https://www.awinet.org

AWS	American Welding Society
https://www.aws.org

AWWA	American Water Works Association
https://www.awwa.org

BHMA	Builders Hardware Manufacturers Association
https://www.buildershardware.com

BIA	The Brick Industry Association
http://www.gobrick.com

CAGI	Compressed Air and Gas Institute
https://www.cagi.org

CGA	Compressed Gas Association, Inc.
https://www.cganet.com

CI		The Chlorine Institute, Inc.
https://www.chlorineinstitute.org

CISCA	Ceilings and Interior Systems Construction Association
https://www.cisca.org

CISPI	Cast Iron Soil Pipe Institute
https://www.cispi.org

CLFMI	Chain Link Fence Manufacturers Institute
https://www.chainlinkinfo.org

CPA	Composite Panel Association

https://www.compositepanel.org

CPMB	Concrete Plant Manufacturers Bureau
https://www.cpmb.org

CRA	California Redwood Association
http://www.calredwood.org

CRSI	Concrete Reinforcing Steel Institute
https://www.crsi.org

CTI	Cooling Technology Institute
https://www.cti.org

DHA	Decorative Hardwoods Association

https://www.decorativehardwoods.org

DHI	Door and Hardware Institute
https://www.dhi.org

EGSA	Electrical Generating Systems Association
http://www.egsa.org

EEI	Edison Electric Institute
https://www.eei.org

EPA	United States Environmental Protection Agency
https://www.epa.gov

ETL	ETL Testing Services
http://www.intertek.com

FAA	Federal Aviation Administration
https://www.faa.gov

FCC	Federal Communications Commission
https://www.fcc.gov

FPS	Forest Products Society
http://www.forestprod.org

GANA	Glass Association of North America
http://www.glasswebsite.com

FM		Factory Mutual Global Insurance
https://www.fmglobal.com

GA		Gypsum Association
https://gypsum.org

GSA	General Services Administration
https://www.gsa.gov

HI		Hydraulic Institute
http://www.pumps.org

ICC	International Code Council
https://shop.iccsafe.org

ICEA	Insulated Cable Engineers Association
https://www.icea.net

ICAC	Institute of Clean Air Companies
http://www.icac.com

IEEE	Institute of Electrical and Electronics Engineers
https://www.ieee.org\

IGMA	Insulating Glass Manufacturers Alliance

https://www.igmaonline.org

IMSA	International Municipal Signal Association
http://www.imsasafety.org

MBMA	Metal Building Manufacturers Association
https://www.mbma.com

MSS	Manufacturers Standardization Society of the Valve and Fittings Industry
http://msshq.org

NAAMM	National Association of Architectural Metal Manufacturers
https://www.naamm.org

PHCC	Plumbing-Heating-Cooling Contractors Association
https://www.phccweb.org

NBS	National Bureau of Standards
See - NIST

NBBI	The National Board of Boiler and Pressure Vessel Inspectors
https://www.nationalboard.org

NEC	National Electric Code
See - NFPA National Fire Protection Association

NEMA	National Electrical Manufacturers Association
https://www.nema.org

NFPA	National Fire Protection Association
https://www.nfpa.org

NHLA	National Hardwood Lumber Association
https://www.nhla.com

NIH	National Institute of Health
https://www.nih.gov

NIST	National Institute of Standards and Technology
https://www.nist.gov

NELMA	Northeastern Lumber Manufacturers Association, Inc.
http://www.nelma.org

NPA	National Particleboard Association
(See CPA, Composite Panel Association)

NSF	National Sanitation Foundation
http://www.nsf.org

OSHA	Occupational Safety and Health Administration
Department of Labor
https://www.osha.gov

PCA	Portland Cement Association
https://www.cement.org

PCI	Precast Prestressed Concrete Institute
https://www.pci.org

PPI	Plastics Pipe Institute
https://www.plasticpipe.org

PEI	Porcelain Enamel Institute
http://www.porcelainenamel.com

PTI	Post-Tensioning Institute
http://www.post-tensioning.org

RFCI	Resilient Floor Covering Institute
https://www.rfci.com

RIS	Redwood Inspection Service
(See Western Wood Products Association)

https://www.wwpa.org

SCMA	Southern Cypress Manufacturers Association
http://www.cypressinfo.org

SDI	Steel Door Institute
http://www.steeldoor.org

SJI	Steel Joist Institute
https://www.steeljoist.org

SMACNA	Sheet Metal & Air-Conditioning Contractors’
National Association
https://www.smacna.org

SSPC	The Society for Protective Coatings
https://www.sspc.org

STI	Steel Tank Institute
https://www.steeltank.com

SWI	Steel Window Institute
https://www.steelwindows.com

TCNA	Tile Council of North America

https://www.tcnatile.com

TEMA	Tubular Exchanger Manufacturers Association
http://www.tema.org

TPI	Truss Plate Institute
https://www.tpinst.org

UBC	The Uniform Building Code
(See ICC)

UL		Underwriters' Laboratories Incorporated
https://www.ul.com

ULC	Underwriters' Laboratories of Canada
https://www.ulc.ca

WCLB	West Coast Lumber Inspection Bureau
http://www.wclib.org

WDMA	Window and Door Manufacturers Association

https://www.wdma.com

WRCLA	Western Red Cedar Lumber Association
https://www.realcedar.com

WWPA	Western Wood Products Association
http://www.wwpa.org

- - - E N D - - -