SECTION 04 20 00
UNIT MASONRY

# PART 1 - GENERAL

# 1.1 DESCRIPTION

This section specifies requirements for construction of masonry unit walls.

# 1.2 RELATED WORK

A.	Mortars: Section 04 05 13, MASONRY MORTARING, Section.

B.	Steel lintels and shelf angles: Section 05 50 00, METAL FABRICATIONS.

C.	Cavity insulation: Section 07 21 13, THERMAL INSULATION.

D.	Flashing: Section 07 60 00, FLASHING AND SHEET METAL.

E.	Sealants and sealant installation: Section 07 92 00, JOINT SEALANTS.

F.	Color and texture of masonry units: Section 09 06 00, SCHEDULE FOR FINISHES.

# 1.3 SUBMITTALS

A.	Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES.

B.	Samples:

1.	Face brick, sample panel, (48 inches by 60 inches,) showing full color range and texture of bricks, bond, and proposed mortar joints. Provide a total of 4 different panels with different proposed bricks to match the existing brick(non-standard size- approximately 8 ¼” x 3 ½” x 2 ¼” VIF)appearance for approval and selection by the VA (sample panels to be reviewed for matching in color, texture, appearance, coursing, mortar, size and matching existing course heights and widths).

2.	Anchors, and ties, one each and joint reinforcing 1200 mm (48 inches) long.

C.	Shop Drawings:

1.	Special masonry shapes.

2.	Drawings, showing reinforcement, applicable dimensions and methods of hanging soffit or lintel masonry and reinforcing masonry for embedment of anchors for hung fixtures. Drawings indicated coursing.

D.	Certificates:

1.	Certificates signed by manufacturer, including name and address of contractor, project location, and the quantity, and date or dates of shipment of delivery to which certificate applies.

2.	Indicating that the following items meet specification requirements:

a.	Face brick.

3.	Testing laboratories facilities and qualifications of its principals and key personnel to perform tests specified.

E.	Laboratory Test Reports:

1.	Brick for pre-built masonry panels.

2.	Ceramic glazed facing brick.

F.	Manufacturer's Literature and Data:

1.	Anchors, ties, and reinforcement.

# 1.4 SAMPLE PANEL

A.	Before starting masonry, lay up a sample panel in accordance with Masonry Standards Joint Committee (MSJC) and Brick Industry Association (BIA).

1.	Use masonry units from random cubes of units delivered on site.

2.	Include reinforcing, ties, and anchors.

B.	Use sample panels approved by COR for standard of workmanship of new masonry work.

C.	Use sample panel to test cleaning methods.

# 1.5 warranty

Warrant exterior masonry walls against moisture leaks and subject to terms of "Warranty of Construction", FAR clause 52.246-21, except that warranty period shall be five years.

# 1.6 APPLICABLE PUBLICATIONS

A.	Publications listed below form a part of this specification to the extent referenced. Publications are referenced in the text by the basic designation only.

B.	American Society for Testing and Materials (ASTM):

A951-06	Steel Wire for Masonry Joint Reinforcement.

A615/A615M-09	Deformed and Plain Billet-Steel Bars for Concrete Reinforcement.

A675/A675M-03(R2009)	Standard Specification for Steel Bars, Carbon, Hot-Wrought, Special Quality, Mechanical PropertiesC34-03	Structural Clay Load-Bearing Wall Tile

C55-09	Concrete Building Brick

C56-10	Structural Clay Non-Load-Bearing Tile

C62-10	Building Brick (Solid Masonry Units Made From Clay or Shale)

C67-09	Sampling and Testing Brick and Structural Clay Tile

C90-11	Load-Bearing Concrete Masonry Units

C126-10	Ceramic Glazed Structural Clay Facing Tile, Facing Brick, and Solid Masonry Units

C216-10	Facing Brick (Solid Masonry Units Made From Clay or Shale)

C476-10	Standard Specification for Grout for Masonry

C612-10	Mineral Fiber Block and Board Thermal Insulation

C744-11	Prefaced Concrete and Calcium Silicate Masonry Units.

D1056-07	Flexible Cellular Materials - Sponge or Expanded Rubber

D2000-08	Rubber Products in Automotive Applications

D2240-05(R2010)	Rubber Property - Durometer Hardness

D3574-08	Flexible Cellular Materials-Slab, Bonded, and Molded Urethane Foams

F1667-11	Fasteners: Nails, Spikes and Staples

C.	Masonry Industry Council:

Hot and Cold Weather Masonry Construction Manual-98 (R2000).

D.	American Welding Society (AWS):

D1.4-11	Structural Welding Code – Reinforcing Steel.

E.	Federal Specifications (FS):

FF-S-107C-00	Screws, Tapping and Drive

F.	Brick Industry Association - Technical Notes on Brick Construction (BIA):

11-2001	Guide Specifications for Brick Masonry, Part I

11A–1988	Guide Specifications for Brick Masonry, Part II

11B–1988	Guide Specifications for Brick Masonry, Part III Execution

11C-1998	Guide Specification for Brick Masonry Engineered Brick Masonry, Part IV

11D-1988	Guide Specifications for Brick Masonry Engineered Brick Masonry, Part IV continued

G.	Masonry Standards Joint Committee; Specifications for Masonry Structures TMS 602-08/ACI 530.1-08/ASCE 6-08 (2008 MSJC Book Version TMS-0402-08).

# PART 2 - PRODUCTS

# 2.1 BRICK

A.	Face Brick:

1.	ASTM C216, Grade SW, Type FBS.

2.	Brick when tested in accordance with ASTM C67: Classified slightly efflorescent or better.

3.	Size:

a.	Modular

b.	Thin Brick: 13 mm (1/2 inch) thick with angle shapes for corners.

B.	Building Brick: ASTM C62, Grade MW for backup and interior work; Grade SW where in contact with earth.

# 2.2 CONCRETE MASONRY UNITS

Concrete Masonry Units (CMU):

Hollow and Solid Load-Bearing Concrete Masonry Units: ASTM C90.

Unit Weight: Normal weight .

# 2.3 CLAY TILE UNITS - NOT USED

# 2.4 SHEAR KEYS -  NOT USED

2.5 ANCHORS, TIES, AND REINFORCEMENT

A.	Steel Reinforcing Bars: ASTM A615M, deformed bars, grade as shown.

B.	Joint Reinforcement: Not Used.

C.	Adjustable Veneer Anchor for Frame Walls:

1.	Two piece, adjustable anchor and tie.

2.	Anchor and tie may be either type; use only one type throughout.

3.	Loop Type:

a.	Anchor: Screw-on galvanized steel anchor strap 2.75 mm (0.11 inch) by 19 mm (3/4 inch) wide by 225 mm (9 inches) long, with 9 mm (0.35 inch) offset and 100 mm (4 inch) adjustment. Provide 5 mm (0.20 inch) hole at each end for fasteners.

b.	Ties: Triangular tie, fabricated of 5 mm (0.20 inch) diameter galvanized cold drawn steel wire. Ties long enough to engage the anchor and be embedded not less than 50 mm (2 inches) into the bed joint of the masonry veneer.

4.	Angle Type:

a.	Anchor: Minimum 2 mm (16 gage) thick galvanized steel angle shaped anchor strap. Provide hole in vertical leg for fastener. Provide hole near end of outstanding leg to suit upstanding portion of tie.

b.	Tie: Fabricate from 5 mm (0.20 inch) diameter galvanized cold drawn steel wire. Form "L" shape to be embedded not less than 50 mm (2 inches) into the bed joint of the masonry veneer and provide upstanding leg to fit through hole in anchor and be long enough to allow 50 mm (2 inches) of vertical adjustment.

D.	Dovetail Anchors:

1.	Corrugated steel dovetail anchors formed of 1.5 mm (0.0598 inch) thick by 25 mm (1 inch) wide galvanized steel, 90 mm (3-1/2 inches) long where used to anchor 100 mm (4 inch) nominal thick masonry units, 140 mm (5-1/2 inches) long for masonry units more than 100 mm (4 inches) thick.

2.	Triangular wire dovetail anchor 100 mm (4 inch) wide formed of 4 mm (9 gage) steel wire with galvanized steel dovetail insert. Anchor length to extend at least 75 mm (3 inches) into masonry, 25 mm (1 inch) into 40 mm (1-1/2 inch) thick units.

3.	Form dovetail anchor slots from 0.6 mm (0.0239 inch) thick galvanized steel (with felt or fiber filler).

E.	Individual ties:

1.	Rectangular ties: Form from 5 mm (3/16 inch) diameter galvanized steel rod to a rectangular shape not less than 50 mm (2 inches) wide by sufficient length for ends of ties to extend within 25 mm (1 inch) of each face of wall. Ties that are crimped to form drip are not permitted.

2.	Adjustable Cavity Wall Ties:

a.	Adjustable seismic wall ties are to be used.

b.	Two piece type permitting up to 40 mm (1-1/2 inch) adjustment.

c.	Form ties from 5 mm (3/16 inch) diameter galvanized steel wire.

d.	Form one piece to a rectangular shape 105 mm (4-1/8 inches) wide by length required to extend into the bed joint 50 mm (2 inches).

e.	Form the other piece to a 75 mm (3 inch) long by 75 mm (3 inch) wide shape, having a 75 mm (3 inch) long bent section for engaging the 105 mm (4-1/8 inch) wide piece to form adjustable connection.

F.	Wall Ties, (Mesh or Wire):

1.	Mesh wall ties formed of ASTM A82, W0.5, 2 mm, (16 gage) galvanized steel wire 13 mm by 13 mm (1/2 inch by 1/2 inch) mesh, 75 mm (3 inches) wide by 200 mm (8 inches) long.

2.	Rectangular wire wall ties formed of W1.4, 3 mm, (9 gage) galvanized steel wire 50 mm (2 inches) wide by 200 mm (8 inches) long.

G.	Corrugated Wall Tie:

1.	Form from 1.5 mm (0.0598 inch) thick corrugated, galvanized steel 30 mm (1-1/4 inches) wide by lengths so as to extend at least 100 mm (4 inches) into joints of new masonry plus 38 mm (1-1/2 inch) turn-up.

2.	Provide 5 mm (3/16 inch) hole in turn-up for fastener attachment.

H.	Adjustable Steel Column Anchor:

1.	Two piece anchor consisting of a 6 mm (1/4 inch) diameter steel rod to be welded to steel with offset ends, rod to permit 100 mm (4 inch) vertical adjustment of wire anchor.

2.	Triangular shaped wire anchor 100 mm (4 inches) wide formed from 5 (3/16 inch) diameter galvanized wire, to extend at least 75 mm (3 inches) into joints of masonry.

# 2.6 PREFORMED COMPRESSIBLE JOINT FILLER

A.	Thickness and depth to fill the joint as specified.

B.	Closed Cell Neoprene: ASTM D1056, Type 2, Class A, Grade 1, B2F1.

C.	Non-Combustible Type: ASTM C612, Class 5, 1800 degrees F.

# 2.7 ACCESSORIES

A.	Weep Hole Wicks: Glass fiber ropes, 10 mm (3/8 inch) minimum diameter, 300 mm (12 inches) long.

B.	Box Board:

1.	Mineral Fiber Board: ASTM C612, Class 1.

2.	25 mm (1 inch) thickness.

3.	Other spacing material having similar characteristics may be used subject to the Resident Engineer's approval.

C.	Masonry Cleaner:

1.	Detergent type cleaner selected for each type masonry used.

2.	Acid cleaners are not acceptable.

3.	Use soapless type specially prepared for cleaning brick or concrete masonry as appropriate.

D.	Fasteners:

1.	Concrete Nails: ASTM F1667, Type I, Style 11, 19 mm (3/4 inch) minimum length.

2.	Masonry Nails: ASTM F1667, Type I, Style 17, 19 mm (3/4 inch) minimum length.

3.	Screws: FS-FF-S-107, Type A, AB, SF thread forming or cutting.

# 2.8 PRE-BUILT MASONRY PANELS - NOT USED

# PART 3 - EXECUTION

# 3.1 JOB CONDITIONS

A.	Protection:

1.	Cover tops of walls with nonstaining waterproof covering, when work is not in progress. Secure to prevent wind blow off.

2.	On new work protect base of wall from mud, dirt, mortar droppings, and other materials that will stain face, until final landscaping or other site work is completed.

B.	Cold Weather Protection:

1.	Masonry may be laid in freezing weather when methods of protection are utilized.

2.	Comply with MSJC and “Hot and Cold Weather Masonry Construction Manual”.

# 3.2 CONSTRUCTION TOLERANCES

A.	Lay masonry units plumb, level and true to line within the tolerances as per MSJC requirements and as follows:

B.	Maximum variation from plumb:

1.	In 3000 mm (10 feet) - 6 mm (1/4 inch).

2.	In 6000 mm (20 feet) - 10 mm (3/8 inch).

3.	In 12 000 mm (40 feet) or more - 13 mm (1/2 inch).

C.	Maximum variation from level:

1.	In any bay or up to 6000 mm (20 feet) - 6 mm (1/4 inch).

2.	In 12 000 mm (40 feet) or more - 13 mm (1/2 inch).

D.	Maximum variation from linear building lines:

1.	In any bay or up to 6000 mm (20 feet) - 13 mm (1/2 inch).

2.	In 12 000 mm (40 feet) or more - 19 mm (3/4 inch).

E.	Maximum variation in cross-sectional dimensions of columns and thickness of walls from dimensions shown:

1.	Minus 6 mm (1/4 inch).

2.	Plus 13 mm (1/2 inch).

F.	Maximum variation in prepared opening dimensions:

1.	Accurate to minus 0 mm (0 inch).

2.	Plus 6 mm (1/4 inch).

# 3.3 INSTALLATION GENERAL

A.	Keep finish work free from mortar smears or spatters, and leave neat and clean.

B.	Anchor masonry as specified in Paragraph, ANCHORAGE.

C.	Wall Openings:

1.	Fill hollow metal frames built into masonry walls and partitions solid with mortar as laying of masonry progresses.

2.	If items are not available when walls are built, prepare openings for subsequent installation.

D.	Tooling Joints:

1.	Do not tool until mortar has stiffened enough to retain thumb print when thumb is pressed against mortar.

2.	Tool while mortar is soft enough to be compressed into joints and not raked out.

3.	Finish joints in exterior face masonry work with a jointing tool, and provide smooth, water-tight concave joint unless specified otherwise.

4.	Tool Exposed interior joints in finish work concave unless specified otherwise.

E.	Partition Height:

1.	Extend partitions at least 100 mm (four inches) above suspended ceiling or to overhead construction where no ceiling occurs.

2.	Extend following partitions to overhead construction.

a.	Where noted smoke partitions, FHP (full height partition), and FP (fire partition) and smoke partitions (SP) on drawings, or as detailed on the Partition Types.

b.	Both walls at expansion joints.

c.	Corridor walls.

d.	Walls at stairway and stair halls, elevators, dumbwaiters, trash and laundry chute shafts, and other vertical shafts.

e.	Walls at refrigerator space.

g.	Reinforced masonry partitions

3.	Extend finish masonry partitions at least four-inches above suspended ceiling and continue with concrete masonry units or structural clay tile to overhead construction:

F.	Lintels:

1.	Lintels are not required for openings less than 1000 mm (3 feet 4 inches) wide that have hollow metal frames.

2.	Openings 1025 mm (3 feet 5 inches) wide to 1600 m (5 feet 4 inches) wide with no structural steel lintel or frames, require a lintel formed of concrete masonry lintel or bond beam units filled with grout per ASTM C476 and reinforced with 1- #15m (1-#5) rod top and bottom for each 100 mm (4 inches) of nominal thickness unless shown otherwise.

3.	Precast lintels of 25 Mpa (3000 psi) concrete, of same thickness as partition, and with one Number 5 deformed bar top and bottom for each 100 mm (4 inches) of nominal thickness, may be used in lieu of reinforced CMU masonry lintels.

4.	Use steel lintels, for openings over 1600 m (5 feet 4 inches) wide, brick masonry, and elevator openings unless shown otherwise.

5.	Doors having overhead concealed door closers require a steel lintel, and a pocket for closer box.

6.	Length for minimum bearing of 100 mm (4 inches) at ends.

7.	Build masonry openings or arches over wood or metal centering and supports when steel lintels are not used.

G.	Wall, Furring, and Partition Units:

1.	Lay out field units to provide for running bond of walls and partitions, with vertical joints in second course centering on first course units unless specified otherwise.

2.	Align head joints of alternate vertical courses.

3.	At sides of openings, balance head joints in each course on vertical center lines of openings.

4.	Use no piece shorter than 100 mm (4 inches) long.

5.	On interior partitions provide a 6 mm (1/4 inch) open joint for caulking between existing construction, exterior walls, concrete work, and abutting masonry partitions.

6.	Use not less than 100 mm (4 inches) nominal thick masonry for free standing furring unless shown otherwise.

7.	Do not abut existing plastered surfaces except suspended ceilings with new masonry partitions.

H.	Use not less than 100 mm (4 inches) nominal thick masonry for fireproofing steel columns unless shown otherwise.

I.	Before connecting new masonry with previously laid, remove loosened masonry or mortar, and clean and wet work in place as specified under wetting.

J. Not Used.

K.	Structural Steel Encased in Masonry: Not Used

L.	Chases: Not Used

M.	Wetting and Wetting Test:

1.	Test and wet brick or clay tile in accordance with BIA 11B.

2.	Do not wet concrete masonry units or glazed structural facing tile before laying.

N.	Temporary Formwork: Provide formwork and shores as required for temporary support of reinforced masonry elements.

O.	Construct formwork to conform to shape, line and dimensions shown. Make sufficiently tight to prevent leakage of mortar, grout, or concrete (if any). Brace, tie and support as required to maintain position and shape during construction and curing of reinforced masonry.

P.	Do not remove forms and shores until reinforced masonry members have hardened sufficiently to carry their own weight and all other reasonable temporary loads that may be placed on them during construction.

# 3.4 ANCHORAGE

A.	Veneer to Frame Walls:

1.	Use adjustable veneer anchors.

2.	Fasten anchor to stud through sheathing with self drilling and tapping screw, one at each end of loop type anchor.

3.	Space anchors not more than 400 mm (16 inches) on center vertically at each stud.

B.	Veneer to Concrete Walls:

1.	Install dovetail slots in concrete vertically at 600 mm (2 feet) on centers.

2.	Locate dovetail anchors at 400 mm (16 inch) maximum vertical intervals.

3.	Anchor new masonry facing to existing concrete with corrugated wall ties spaced at 400 mm, (16 inch) maximum vertical intervals, and at 600 mm (2 feet) maximum horizontal intervals. Fasten ties to concrete with power actuated fasteners or concrete nails.

C.	Masonry Facing to Backup and Cavity Wall Ties: (Where Applicable)

1.	Use individual ties for new work.

2.	Stagger ties in alternate courses, and space at 400 mm (16 inches) maximum vertically, and 600 mm (2 feet) horizontally.

3.	At openings, provide additional ties spaced not more than 900 mm (3 feet) apart vertically around perimeter of opening, and within 300 mm (12 inches) from edge of opening.

4.	Anchor new masonry facing to existing masonry with corrugated wall ties spaced at 400 mm (16 inch) maximum vertical intervals and at every second masonry unit horizontally. Fasten ties to masonry with masonry nails.

5.	Option: Use joint reinforcing for multiple wythes and cavity wall ties spaced not more than 400 mm (16 inches) vertically.

6.	Tie interior and exterior wythes of reinforced masonry walls together with individual ties. Provide ties at intervals not to exceed 600 mm (24 inches) on center horizontally, and 400 mm (16 inches) on center vertically. Lay ties in the same line vertically in order to facilitate vibrating of the grout pours.

D.	Anchorage of Abutting Masonry:

1.	Anchor interior 100 mm (4 inch) thick masonry partitions to exterior masonry walls with wall ties. Space ties at 600 mm (2 foot) maximum vertical intervals. Extend ties 100 mm (4 inches) minimum into masonry.

2.	Anchor interior masonry bearing walls or interior masonry partitions over 100 mm (4 inches) thick to masonry walls with rigid wall anchors spaced at 400 mm (16 inch) maximum vertical intervals.

3.	Anchor abutting masonry walls and partitions to concrete with dovetail anchors. Install dovetail slots vertically in concrete at centerline of abutting wall or partition. Locate dovetail anchors at 400 mm (16 inch) maximum vertical intervals. Secure anchors to existing wall with two 9 mm (3/8 inch) by 75 mm (3 inch) expansion bolts or two power-driven fasteners.

4.	Anchor abutting interior masonry partitions to existing concrete and existing masonry construction, with corrugated wall ties. Extend ties at least 100 mm (4 inches) into joints of new masonry. Fastened to existing concrete and masonry construction, with powder actuated drive pins, nail or other means that provides rigid anchorage. Install anchors at 400 mm (16 inch) maximum vertical intervals.

E.	Masonry Furring:

1.	Anchor masonry furring less than 100 mm (4 inches) nominal thick to masonry walls or to concrete with corrugated wall ties or dovetail anchors.

2.	Space not over 600 mm (2 feet) on centers in both directions.

F.	Anchorage to Steel Beams or Column: Not Used

# 3.5 REINFORCEMENT

A.	Joint Reinforcement:

1.	Use as joint reinforcement in CMU wythe of combination brick and CMU, cavity walls, and single wythe concrete masonry unit walls or partitions.

2.	Reinforcing may be used in lieu of individual ties for anchoring brick facing to CMU backup in exterior masonry walls.

3.	Brick veneer over frame backing walls does not require joint reinforcement.

4.	Locate joint reinforcement in mortar joints at 400 mm (16 inch) maximum vertical intervals.

5.	Additional joint reinforcement is required in mortar joints at both 200 mm (8 inches) and 400 (16 inches) above and below windows, doors, louvers and similar openings in masonry, except where other type anchors are required for anchorage of masonry to concrete structure.

6.	Joint reinforcement is required in every other course of stack bond CMU masonry.

7.	Wherever brick masonry is backed up with stacked bond masonry, joint reinforcement is required in every other course of CMU backup, and in corresponding joint of facing brick.

B.	Steel Reinforcing Bars: Not Used

# 3.6 BRICK EXPANSION AND CMU CONTROL JOINTS. Not Used

# 3.7 BUILDING EXPANSION AND SEISMIC JOINTS. Not Used

# 3.8 ISOLATION SEAL.

A.	Where full height walls or partitions lie parallel or perpendicular to and under structural beams or shelf angles, provide a separation between walls or partitions and bottom of beams or shelf angles not less than the masonry joint thickness unless shown otherwise.

B.	Insert in the separation, a continuous full width strip of non-combustible type compressible joint filler.

C.	Where exposed in finish work, cut back filler material in the joint enough to allow for the joint to be filled with sealant material specified in Section 07 92 00, JOINT SEALANTS.

# 3.9 BRICKWORK

A.	Lay clay brick in accordance with BIA Technical Note 11 series.

B.	Laying:

1.	Lay brick in running bond with course of masonry bonded at corners unless shown otherwise. Match bond of existing building on alterations and additions.

2.	Maintain bond pattern throughout.

3.	Do not use brick smaller than half-brick at any angle, corner, break or jamb.

4.	Where length of cut brick is greater than one half but less than a whole brick, maintain the vertical joint location of such units.

5.	Lay exposed brickwork joints symmetrical about center lines of openings.

6.	Do not structural bond multi wythe brick walls unless shown.

7.	Before starting work, lay facing brick on foundation wall and adjust bond to openings, angles, and corners.

8.	Lay brick for sills with wash and drip.

9.	Build solid brickwork as required for anchorage of items.

C.	Joints:

1.	Exterior and interior joint widths: Lay for three equal joints in 200 mm (eight inches) vertically, unless shown otherwise.

2.	Rake joints for pointing with colored mortar when colored mortar is not full depth.

3.	Arches:

a.	Flat arches (jack arches) lay with camber of 1 in 200 (1/16 inch per foot) of span.

b.	Face radial arches with radial brick with center line of joints on radial lines.

c.	Form Radial joints of equal width.

d.	Bond arches into backing with metal ties in every other joint.

D.	Weep Holes:

1.	Install weep holes at 600 mm (24 inches) on center in bottom of vertical joints of exterior masonry veneer or cavity wall facing over foundations, bond beams, and other water stops in the wall.

2.	Form weep holes using wicks made of mineral fiber insulation strips turned up 200 mm (8 inches) in cavity. Anchor top of strip to backup to securely hold in place.

3.	Install sand or pea gravel in cavity approximately 75 mm (3 inches) high between weep holes.

E.	Solid Exterior Walls: Not Used

F.	Cavity Type Exterior Walls: Not Used

# 3.10 CONCRETE MASONRY –

        - Types and Uses:

Provide special concrete masonry shapes as required, including lintel. Provide solid concrete masonry units, where full units cannot be installed, or where needed for anchorage of accessories.

Provide solid load-bearing concrete masonry units or grout cell of hollow units at jambs of openings in walls, where structural members impose loads directly on concrete masonry, and where shown.

Provide rounded corner (bullnose) shapes at opening jambs in exposed work and at exterior corners.

Do not install brick jambs in exposed finish work.

Install concrete building brick only as filler in backup material where not exposed.

Construct fire resistance in fire rated partitions meeting fire ratings indicated on drawings.

Structural Clay Tile Units (Not Used):

Laying:

Lay concrete masonry units with 9 mm (3/8 inch) joints, with a bond overlap of minimum 1/4 of unit length, except where stack bond is indicated on drawings.

Do not wet concrete masonry units before laying.

Bond external corners of partitions by overlapping alternate courses.

Lay first course in a full mortar bed.

Set anchorage items as work progress.

Where ends of anchors, bolts, and other embedded items, project into voids of units, completely fill voids with mortar or grout.

Provide 6 mm (1/4 inch) open joint for sealant between existing construction, exterior walls, concrete work, and abutting masonry partitions.

Lay concrete masonry units with full face shell mortar beds and fill head joint beds for depth equivalent to face shell thickness.

Lay concrete masonry units so cores of units, that are to be filled with grout, are vertically continuous with joints of cross webs of such cores completely filled with mortar. Unobstructed core openings minimum 50 mm (2 inches) by 75 mm (3 inches).

Do not wedge masonry against steel reinforcing. Minimum 13 mm (1/2 inch) clear distance between reinforcing and masonry units.

Install deformed reinforcing bars of sizes indicated on drawings.

At time of placement, ensure steel reinforcement is free of loose rust, mud, oil, and other contamination capable of affecting bond.

Place steel reinforcement at spacing indicated on drawings before grouting.

Minimum clear distance between parallel bars: One bar diameter.

Hold vertical steel reinforcement in place vertically by centering clips, caging devices, tie wire, or other approved methods.

Support vertical bars near each end and at maximum 192 bar diameter on center.

Splice reinforcement or attach reinforcement to dowels by placing in contact and securing with wire ties.

Stagger splices in adjacent horizontal reinforcing bars. Lap reinforcing bars at splices a minimum of 40 bar diameters.

Grout cells of concrete masonry units, containing reinforcing bars, solid as specified.

Install cavity and joint reinforcement as masonry work progresses.

Rake joints 6 to 10 mm (1/4 to 3/8 inch) deep for pointing with colored mortar when colored mortar is not full depth.

Waterproofing Parging:

Parge earth side of concrete masonry unit basement walls with mortar applied in two coats, each coat 6 mm (1/4 inch) thick.

Clean wall surfaces to receive parging of dirt, oil, or grease, and moisten before application of first coat.

Roughen first coat when partially set, permit to hardened for 24 hours, and moisten before application of second coat.

Keep second coat damp for minimum 48 hours.

Thicken parging and round to form a cove at the junction of outside wall face and footing.

# 3.11 GLAZED STRUCTURAL FACING TILE (GSFT) - NOT USED

# 3.12 POINTING - NOT USED

# 3.13 GROUTING

A.	Preparation:

1.	Clean grout space of mortar droppings before placing grout.

2.	Close cleanouts.

3.	Install vertical solid masonry dams across grout space for full height of wall at intervals of not more than 9000 mm (30 feet). Do not bond dam units into wythes as masonry headers.

4.	Verify reinforcing bars are in cells of units or between wythes as shown.

B.	Placing:

1.	Place grout by hand bucket, concrete hopper, or grout pump.

2.	Consolidate each lift of grout after free water has disappeared but before plasticity is lost.

3.	Do not slush with mortar or use mortar with grout.

4.	Interruptions:

a.	When grouting must be stopped for more than an hour, top off grout 40 mm (1-1/2 inch) below top of last masonry course.

b.	Grout from dam to dam on high lift method.

c.	A longitudinal run of masonry may be stopped off only by raking back one-half a masonry unit length in each course and stopping grout 100 mm (4 inches) back of rake on low lift method.

C.	Puddling Method:

1.	Double wythe masonry constructed grouted in lifts not to exceed 300 mm (12 inches) or less than 50 mm (2 inches) wide.

2.	Consolidate by puddling with a grout stick during and immediately after placing.

3.	Grout the cores of concrete masonry units containing the reinforcing bars solid as the masonry work progresses.

D.	Low Lift Method:

1.	Construct masonry to a height of 1.5 m (5 ft) maximum before grouting.

2. Grout in one continuous operation and consolidate grout by mechanical vibration and reconsolidate after initial water loss and settlement has occurred.

E.	High Lift Method:

1.	Do not pour grout until masonry wall has properly cured a minimum of 4 hours.

2.	Place grout in lifts not exceeding 1.5 m (5 ft).

3.	Exception:

Where the following conditions are met, place grout in lifts not exceeding 3.86 m (12.67 ft).

a.	The masonry has cured for at least 4 hours.

b.	The grout slump is maintained between 254 and 279 mm (10 and 11 in).

c.	No intermediate reinforced bond beams are placed between the top and the bottom of the pour height.

4.	When vibrating succeeding lifts, extend vibrator 300 to 450 mm (12 to 18 inches) into the preceding lift to close any shrinkage cracks or separation from the masonry units.

3.14 PLACING REINFORCEMENT

        - General: Clean reinforcement of loose rust, mill scale, earth, ice or

- other materials which will reduce bond to mortar or grout. Do not use reinforcement bars with kinks or bends not shown on drawings or approved submittal drawings, or bars with reduced cross-section due to excessive rusting or other causes.

        - Position reinforcement accurately at spacing indicated on drawings. Support and secure vertical bars against displacement. Install horizontal reinforcement as masonry work progresses. Where vertical bars are shown in close proximity, provide clear distance between bars of minimum one bar diameter or 25 mm (1 inch), whichever is greater

        - Embed metal ties in mortar joints as work progresses, with minimum mortar cover of 15 mm (5/8 inch) on exterior face of walls and 13 mm (1/2 inch) at other locations.

3.15 INSTALLATION OF REINFORCED BRICK MASONRY

A.	Mortar Jointing and Bedding:

1.	Pattern Bond: Lay exterior wythes in the pattern bond shown, or if not shown, lay in 1/2 running bond with vertical joints in each course centered on units in courses above and below. Lay inner wythes (if any) with all units in a wythe bonded by lapping not less than 50 mm (2 inches). Bond and interlock each course of each wythe at corners and intersections. Do not use units with less than 100 mm (4 inch) nominal horizontal face dimension at corners or jambs.

2.	Lay exterior wythes with bed (horizontal) and head (vertical) joints between units completely filled with mortar. Top of bed joint mortar may be sloped toward center of walls. Butter ends of units with sufficient mortar to completely fill head joints and shove into place.  Do not furrow bed joints or slush head joints. Remove any mortar fins which protrude into grout space.

3.	Maintain joint widths shown for head and bed joints, except for minor variations required to maintain pattern bond. If not shown, lay with 10 mm (3/8 inch) head and bed joints.

3.16 INSTALLATION OF REINFORCED CONCRETE UNIT MASONRY – NOT USED

# 3.17 CLEANING AND REPAIR

A.	General:

1.	Clean exposed masonry surfaces on completion.

2.	Protect adjoining construction materials and landscaping during cleaning operations.

3.	Cut out defective exposed new joints to depth of approximately 19 mm (3/4 inch) and repoint.

4.	Remove mortar droppings and other foreign substances from wall surfaces.

B.	Brickwork:

1.	First wet surfaces with clean water, then wash down with a solution of soapless detergent. Do not use muriatic acid.

2.	Brush with stiff fiber brushes while washing, and immediately thereafter hose down with clean water.

3.	Free clean surfaces of traces of detergent, foreign streaks, or

# 3.18 WATER PENETRATION TESTING – Not used

- - - E N D - - -