SECTION 08 14 00

INTERIOR WOOD DOORS

GENERAL

SUMMARY

Section Includes:

Interior flush wood doors transparent finish.

Fire rated doors.

Smoke rated doors.

Interior stile and rail wood doors transparent finish.

RELATED REQUIREMENTS

Paints and Coatings and Composite Wood and Agrifiber VOC Limits: Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS.

Door Hardware including hardware location (height): Section 08 71 00, DOOR HARDWARE.

Installation of Doors and Hardware: Section 08 11 13, HOLLOW METAL DOORS AND FRAMES, Section 08 71 00, DOOR HARDWARE.

Door Finish: Section 09 06 00, SCHEDULE FOR FINISHES.

APPLICABLE PUBLICATIONS

Comply with references to extent specified in this section.

American National Standards Institute/Window and Door Manufacturers Association (ANSI/WDMA):

I.S. 1A-13 - Architectural Wood Flush Doors.

I.S. 6A-13 - Interior Architectural Stile and Rails Doors.

ASTM International (ASTM):

E90-09 - Laboratory Measurements of Airborne Sound Transmission Loss of Building Partitions and Elements.

National Fire Protection Association (NFPA):

80-16 - Fire Doors and Other Opening Protectives.

252-12 - Fire Tests of Door Assemblies.

UL LLC (UL):

10C-09 - Positive Pressure Fire Tests of Door Assemblies.

Window and Door Manufacturers Association (WDMA):

TM 7-14 - Cycle-Slam Test.

TM 8-14 - Hinge Loading Test.

TM 10-14 - Screw Holding Capacity.

SUBMITTALS

Submittal Procedures: Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

Submittal Drawings:

Show size, configuration, and fabrication and installation details.

Include details of glazing.

Indicate project specific requirements not included in Manufacturer's Literature and Data submittal.

Manufacturer's Literature and Data:

Description of each product.

Fire rated doors showing conformance with NFPA 80.

Samples:

Corner section of flush veneered door 300 mm (12 inches) square, showing details of construction, labeled to show grade and type number and conformance to specified standard.

Veneer sample 200 mm by 275 mm (8 inch by 11 inch) showing specified wood species sanded to receive a transparent finish. Factory finish veneer sample where the prefinished option is accepted.

Sustainable Construction Submittals:

Low Pollutant-Emitting Materials:

Show volatile organic compound types and quantities.

Test Reports: Indicate each product complies with specifications.

Screw Holding Capacity Test.

Cycle-Slam Test.

Hinge-Loading Test.

Operation and Maintenance Data:

Care instructions for each exposed finish product.

QUALITY ASSURANCE

Manufacturer Qualifications:

Regularly and presently manufactures specified products.

Manufactures specified products with satisfactory service on five similar installations for minimum five years.

DELIVERY

Deliver products in manufacturer's original sealed packaging.

Minimum 0.15 mm (6 mil) polyethylene bags or cardboard packaging to remain unbroken during delivery and storage.

Mark packaging, legibly. Indicate manufacturer's name or brand, type, and manufacture date.

Identify door opening corresponding to Door Schedule.

Before installation, return or dispose of products within distorted, damaged, or opened packaging.

STORAGE AND HANDLING

Store products indoors in dry, weathertight, conditioned facility.

Store doors according to ANSI/WDMA I.S. 1A.

Protect products from damage during handling and construction operations.

FIELD CONDITIONS

Environment:

Product Temperature: Minimum 21 degrees C (70 degrees F) for minimum 48 hours before installation.

Work Area Ambient Temperature Range: 21 to 27 degrees C (70 to 80 degrees F) continuously, beginning 48 hours before installation.

Install products when building is permanently enclosed and when wet construction is completed, dried, and cured.

Comply with door manufacturer's instructions for relative humidity.

WARRANTY

Construction Warranty: FAR clause 52.246-21, "Warranty of Construction."

Manufacturer's Warranty: Warrant interior factory finished flush stile and rail wood doors against material and manufacturing defects for a period of five (5) years.

PRODUCTS

PRODUCTS - GENERAL

Basis of Design: Section 09 06 00, SCHEDULE FOR FINISHES.

Provide each product from one manufacturer.

Sustainable Construction Requirements:

Low Pollutant-Emitting Materials: Comply with VOC limits specified in Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS for the following products:

Paints and coatings.

Composite wood and agrifiber.

FLUSH WOOD DOORS

General:

ANSI/WDMA I.S. 1A, Extra Heavy Duty.

Adhesive: Type II.

Core: Structural composite lumber, except when mineral core is required for fire rating.

Thickness: 44 mm (1-3/4 inches) unless otherwise shown or specified.

Faces:

ANSI/WDMA I.S. 1A.

One species throughout project unless scheduled or otherwise shown.

Transparent Finished Faces: Premium Grade. rotary cut, white birch.

AA Grade face veneer.

Door Edges: Same species as door face veneer, except maple is acceptable for stile face veneer on birch doors.

In existing buildings, where doors are required to have transparent finish, use wood species, grade, and assembly of face veneers to match adjacent existing doors.

Factory sand doors for finishing.

Stiles and Rails:

Composite material having screw withdrawal force greater than minimum performance level value when tested according to WDMA TM 10.

Provide adequate blocking for bottom of doors having mechanically operated door bottom seal meeting or exceeding performance duty level per WDMA TM 10 for horizontal door edge screw holding.

Fire-Rated Wood Doors:

Fire Resistance Rating:

B Label: 1-1/2 hours.

Labels:

Comply with NFPA 252, UL 10C, and labeled by qualified testing and inspection agency showing fire resistance rating.

Metal labels with raised or incised markings.

Performance Criteria for Stiles of Doors Utilizing Standard Mortise Leaf Hinges:

Hinge Loading: WDMA TM 8. Average of 10 test samples for Extra Heavy Duty doors.

Direct Screw Withdrawal: WDMA TM 10 for Extra Heavy Duty doors. Average of 10 test samples using a steel, fully threaded #12 wood screw.

Cycle-Slam: 1,000,000 cycles with no loose hinge screws or other visible signs of failure when tested according to WDMA TM 7.

Hardware Reinforcement:

Provide fire rated doors with hardware reinforcement blocking.

Size of lock blocks as required to secure hardware specified.

Top, Bottom and Intermediate Rail Blocks: Minimum 125 mm (5 inches) by full core width.

Reinforcement blocking in compliance with labeling requirements.

Mineral material similar to core is not acceptable.

Other Core Components: Manufacturer's standard as allowed by labeling requirements.

Glazed Vision Panel Frame: Steel approved for use in labeled doors.

Astragal: Steel type for pairs of doors.

Smoke Barrier Doors:

Glazed Vision Panel Frame: Steel approved for use in labeled doors.

Astragal: Steel type for pairs of doors, including double egress doors.

FABRICATION

Factory machine interior wood doors to receive hardware, bevels, undercuts, cutouts, accessories and fitting for frame.

Factory fit fire rated doors according to NFPA 80.

Rout doors for hardware using templates and location heights specified in Section 08 71 00, DOOR HARDWARE.

Factory fit doors to frame, bevel lock edge of doors 3 mm (1/8 inch) for each 50 mm (2 inches) of door thickness // undercut where shown //.

Clearances between Doors and Frames and Floors:

Fire Rated Doors: Comply with NFPA 80.

Doors with Automatic Bottom Seal: Maximum clearance 10 mm (3/8 inch) at threshold.

Other Door Bottoms: Maximum 3 mm (1/8 inch) clearance at the jambs, heads, and meeting stiles, and a 19 mm (3/4 inch) clearance at bottom, except as otherwise specified.

Door Jambs, Heads, and Meeting Stiles: Maximum 3 mm (1/8 inch).

Provide cutouts for glazed openings.

Finish surfaces, including both faces, top and bottom and edges of the doors smooth to touch.

Identify each door on top edge.

Mark with stamp, brand or other indelible mark, giving manufacturer’s name, door’s trade name, construction of door, date of manufacture and quality.

Mark door or provide separate certification including name of inspection organization.

Identify door manufacturing standard, including glue type.

Identify veneer and quality certification.

FINISHES

Factory Transparent Finish:

Factory finish flush wood doors.

ANSI/WDMA I.S. 1A Section F-3 Finish System Descriptions for System 5, Conversion Varnish or System 7, Catalyzed Vinyl.

Use stain when required to produce finish specified in Section 09 06 00, SCHEDULE FOR FINISHES.

EXECUTION

PREPARATION

Examine and verify substrate suitability for product installation.

Verify door frames are properly anchored.

Verify door frames are plumb, square, in plane, and within tolerances for door installation.

Protect existing construction and completed work from damage.

Install astragal on active leaf of pair of smoke doors and one leaf of double egress smoke doors.

INSTALLATION

Install products according to manufacturer's instructions and approved submittal drawings.

Install fire rated doors according to NFPA 80.

When manufacturer's instructions deviate from specifications, submit proposed resolution for Contracting Officer's Representative consideration.

PROTECTION

After installation, place shipping container over door and tape in place.

Do not apply tape to door faces and edges.

Provide protective covering over exposed hardware in addition to covering door.

Maintain covering in good condition until removal is directed by Contracting Officer's Representative.

- - E N D - -