SECTION 08 71 00
DOOR HARDWARE

PART 1 - GENERAL

1.1 DESCRIPTION

A.	Door hardware and related items necessary for complete installation and operation of doors.

1.2 RELATED WORK

A.	Caulking: Section 07 92 00 JOINT SEALANTS.

B.	Application of Hardware: Section 08 14 00, WOOD DOORS Section 08 11 13, HOLLOW METAL DOORS AND FRAMES: Section 09 06 00, SCHEDULE FOR FINISHES.

C.	Painting: Section 09 91 00, PAINTING.

1.3 GENERAL

A.	All hardware shall comply with UFAS, (Uniform Federal Accessible Standards) unless specified otherwise.

B.	Provide rated door hardware assemblies where required by most current version of the International Building Code (IBC).

C.	Hardware for Labeled Fire Doors and Exit Doors: Conform to requirements of NFPA 80 for labeled fire doors and to NFPA 101 for exit doors, as well as to other requirements specified. Provide hardware listed by UL, except where heavier materials, large size, or better grades are specified herein under paragraph HARDWARE SETS. In lieu of UL labeling and listing, test reports from a nationally recognized testing agency may be submitted showing that hardware has been tested in accordance with UL test methods and that it conforms to NFPA requirements.

D.	Hardware for application on metal and wood doors and frames shall be made to standard templates. Furnish templates to the fabricator of these items in sufficient time so as not to delay the construction.

E.	The following items shall be of the same manufacturer, except as otherwise specified:

1.	Mortise locksets.

2.	Hinges for hollow metal and wood doors.

3.	Exit devices.

1.4 WARRANTY

A.	Door hardware shall be subject to the terms of FAR Clause 52.246-21, except that the Warranty period shall be two years in lieu of one year for all items except as noted below:

1.	Locks, latchsets, and panic hardware: 5 years.

2.	Door closers and continuous hinges: 10 years.

1.5 MAINTENANCE MANUALS

A.	In accordance with Section 01 00 00, GENERAL REQUIREMENTS Article titled "INSTRUCTIONS", furnish maintenance manuals and instructions on all door hardware. Provide installation instructions with the submittal documentation.

1.6 SUBMITTALS

A.	Submittals shall be in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES. Submit 6 copies of the schedule per Section 01 33 23. Submit 2 final copies of the final approved schedules to VAMC Locksmith as record copies (VISN Locksmith if the VAMC does not have a locksmith).

B.	Hardware Schedule: Prepare and submit hardware schedule in the following form:

| Hardware Item | Quantity | Size | Reference Publication Type No. | Finish | Mfr. Name and Catalog No. | Key Control Symbols | UL Mark (if fire rated and listed) | ANSI/BHMA Finish Designation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

C.	Samples and Manufacturers' Literature:

1.	Samples: All hardware items (proposed for the project) that have not been previously approved by Builders Hardware Manufacturers Association shall be submitted for approval. Tag and mark all items with manufacturer's name, catalog number and project number.

2.	Samples are not required for hardware listed in the specifications by manufacturer's catalog number, if the contractor proposes to use the manufacturer's product specified.

D.	Certificate of Compliance and Test Reports: Submit certificates that hardware conforms to the requirements specified herein. Certificates shall be accompanied by copies of reports as referenced. The testing shall have been conducted either in the manufacturer's plant and certified by an independent testing laboratory or conducted in an independent laboratory, within four years of submittal of reports for approval.

1.7 DELIVERY AND MARKING

A.	Deliver items of hardware to job site in their original containers, complete with necessary appurtenances including screws, keys, and instructions. Tag one of each different item of hardware and deliver to Resident Engineer for reference purposes. Tag shall identify items by Project Specification number and manufacturer's catalog number. These items shall remain on file in Resident Engineer's office until all other similar items have been installed in project, at which time the Resident Engineer will deliver items on file to Contractor for installation in predetermined locations on the project.

1.8 preinstallation meeting

A.	Convene a preinstallation meeting not less than 30 days before start of installation of door hardware.  Require attendance of parties directly affecting work of this section, including Contractor and Installer, Architect, Project Engineer and VA Locksmith, Hardware Consultant, and Hardware Manufacturer’s Representative.  Review the following:

1.	Inspection of door hardware.

2.	Job and surface readiness.

3.	Coordination with other work.

4.	Protection of hardware surfaces.

5.	Substrate surface protection.

6.	Installation.

7.	Adjusting.

8.	Repair.

9.	Field quality control.

10. Cleaning.

1.9 INSTRUCTIONS

A.	Hardware Set Symbols on Drawings: Except for protective plates, door stops, mutes, thresholds and the like specified herein, hardware requirements for each door are indicated on drawings by symbols. Symbols for hardware sets consist of letters (e.g., "HW") followed by a number. Each number designates a set of hardware items applicable to a door type.

B.	Keying: All cylinders shall be keyed into existing Grand Master Key System. Provide removable core cylinders that are removable only with a special key or tool without disassembly of knob or lockset. Cylinders shall be  6  pin type. Keying information shall be furnished at a later date by the C.O.R.

1.10 APPLICABLE PUBLICATIONS

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only. In text, hardware items are referred to by series, types, etc., listed in such specifications and standards, except as otherwise specified.

B.	American Society for Testing and Materials (ASTM):

F883-04	Padlocks

E2180-07................Standard Test Method for Determining the Activity of Incorporated Antimicrobial Agent(s) In Polymeric or Hydrophobic Materials

C.	American National Standards Institute/Builders Hardware Manufacturers Association (ANSI/BHMA):

A156.1-06	Butts and Hinges

A156.2-03	Bored and Pre-assembled Locks and Latches

A156.3-08	Exit Devices, Coordinators, and Auto Flush Bolts

A156.4-08	Door Controls (Closers)

A156.5-14	Cylinders and Input Devices for Locks.

A156.6-05	Architectural Door Trim

A156.8-05	Door Controls-Overhead Stops and Holders

A156.11-14	Cabinet Locks

A156.12-05 .............Interconnected Locks and Latches

A156.13-05	Mortise Locks and Latches Series 1000

A156.14-07 .............Sliding and Folding Door Hardware

A156.15-06	Release Devices-Closer Holder, Electromagnetic and Electromechanical

A156.16-08	Auxiliary Hardware

A156.17-04 .............Self-Closing Hinges and Pivots

A156.18-06	Materials and Finishes

A156.20-06 .............Strap and Tee Hinges, and Hasps

A156.21-09	Thresholds

A156.22-05	Door Gasketing and Edge Seal Systems

A156.23-04	Electromagnetic Locks

A156.24-03	Delayed Egress Locking Systems

A156.25-07 .............Electrified Locking Devices

A156.26-06	Continuous Hinges

A156.28-07 .............Master Keying Systems

A156.29-07 .............Exit Locks and Alarms

A156.30-03 .............High Security Cylinders

A156.31-07 	Electric Strikes and Frame Mounted Actuators

A156.36-10	Auxiliary Locks

A250.8-03	Standard Steel Doors and Frames

D.	National Fire Protection Association (NFPA):

80-10	Fire Doors and Fire Windows

101-09	Life Safety Code

E.	Underwriters Laboratories, Inc. (UL):

Building Materials Directory (2008)

PART 2 - PRODUCTS

2.1   BUTT HINGES

A.	ANSI A156.1. Provide only three-knuckle hinges, except five-knuckle where the required hinge type is not available in a three-knuckle version (e.g., some types of swing-clear hinges). The following types of butt hinges shall be used for the types of doors listed, except where otherwise specified:

1.	Exterior Doors: Type A2112/A5112 for doors 900 mm (3 feet) wide or less and Type A2111/A5111 for doors over 900 mm (3 feet) wide. Hinges for exterior outswing doors shall have non-removable pins.  Hinges for exterior fire-rated doors shall be of stainless steel material.

2.	Interior Doors: Type A8112/A5112 for doors 900 mm (3 feet) wide or less and Type A8111/A5111 for doors over 900 mm (3 feet) wide.  Hinges for doors exposed to high humidity areas (shower rooms, toilet rooms, kitchens, janitor rooms, etc. shall be of stainless steel material.

B.	Provide quantity and size of hinges per door leaf as follows:

- Doors up to 1210 mm (4 feet) high:  2 hinges.

- Doors 1210 mm (4 feet) to 2260 mm (7 feet 5 inches) high:  3 hinges minimum.

- Doors greater than 2260 mm (7 feet 5 inches) high:  4 hinges.

- Doors up to 900 mm (3 feet) wide, standard weight:  114 mm x 114 mm (4-1/2 inches x 4-1/2 inches) hinges.

- Doors over 900 mm (3 feet) to 1065 mm (3 feet 6 inches) wide, standard weight: 127 mm x 114 mm (5 inches x 4-1/2 inches).

- Doors over 1065 mm (3 feet 6 inches) to 1210 mm (4 feet), heavy weight:  127 mm x 114 mm (5 inches x 4-1/2 inches).

- Provide heavy-weight hinges where specified.

- At doors weighing 330 kg (150 lbs.) or more, furnish 127 mm (5 inch) high hinges.

C.	See Articles "MISCELLANEOUS HARDWARE" and "HARDWARE SETS" for pivots and hinges other than butts specified above and continuous hinges specified below.

2.2 DOOR CLOSING DEVICES

A.	Closing devices shall be products of one manufacturer for each type specified.

2.3 DOOR STOPS

A.	Conform to ANSI A156.16.

B.	Provide door stops wherever an opened door or any item of hardware thereon would strike a wall, column, equipment or other parts of building construction. For concrete, masonry or quarry tile construction, use lead expansion shields for mounting door stops.

C.	Where cylindrical locks with turn pieces or pushbuttons occur, equip wall bumpers Type L02251 (rubber pads having concave face) to receive turn piece or button.

D.	Provide floor stops (Type L02141 or L02161 in office areas; Type L02121 x 3 screws into floor elsewhere. Wall bumpers, where used, must be installed to impact the trim or the door within the leading half of its width.  Floor stops, where used, must be installed within 4-inches of the wall face and impact the door within the leading half of its width.

E.	Where drywall partitions occur, use floor stops, Type L02141 or L02161 in office areas, Type L02121 elsewhere.

F.	Provide stop Type L02011, as applicable for exterior doors.  At outswing doors where stop can be installed in concrete, provide stop mated to concrete anchor set in 76mm (3-inch) core-drilled hole and filled with quick-setting cement.

G.	Omit stops where floor mounted door holders are required and where automatic operated doors occur.

H.	Provide appropriate roller bumper for each set of doors (except where closet doors occur) where two doors would interfere with each other in swinging.

I.	Provide appropriate door mounted stop on doors in individual toilets where floor or wall mounted stops cannot be used.

J.	Provide overhead surface applied stop Type C02541, ANSI A156.8 on patient toilet doors in bedrooms where toilet door could come in contact with the bedroom door.

K.	Provide door stops on doors where combination closer magnetic holders are specified, except where wall stops cannot be used or where floor stops cannot be installed within 4-inches of the wall.

L.	Where the specified wall or floor stop cannot be used, provide concealed overhead stops (surface-mounted where concealed cannot be used).

2.4   LOCKS AND LATCHES

A.	Conform to ANSI A156.2. Locks and latches for doors 45 mm (1-3/4 inch) thick or over shall have beveled fronts. Lock cylinders shall have not less than six pins. Cylinders for all locksets shall be removable core type. Cylinders shall be furnished with construction removable cores and construction master keys. Cylinder shall be removable by special key or tool. Construct all cores so that they will be interchangeable into the core housings of all mortise locks, rim locks, cylindrical locks, and any other type lock included in the Great Grand Master Key System. Disassembly of lever or lockset shall not be required to remove core from lockset. All locksets or latches on double doors with fire label shall have latch bolt with 19 mm (3/4 inch) throw, unless shorter throw allowed by the door manufacturer’s fire label. Provide temporary keying device or construction core of allow opening and closing during construction and prior to the installation of final cores.

B.	In addition to above requirements, locks and latches shall comply with following requirements:

1.	Mortise Lock and Latch Sets: Conform to ANSI/BHMA A156.13. Mortise locksets shall be series 2000, minimum Grade 2. All locksets and latchsets, except on designated doors in Psychiatric (Mental Health) areas, shall have lever handles fabricated from cast stainless steel.  Provide sectional (lever x rose) lever design matching [ML 2000]. No substitute lever material shall be accepted. All locks and latchsets shall be furnished with 122.55 mm (4-7/8-inch) curved lip strike and wrought box. At outswing pairs with overlapping astragals, provide flat lip strip with 21mm (7/8-inch) lip-to-center dimension.  Lock function F02 shall be furnished with emergency tools/keys for emergency entrance. Furnish armored fronts for all mortise locks.  Where mortise locks are installed in high-humidity locations or where exposed to the exterior on both sides of the opening, provide non-ferrous mortise lock case.

3.	Auxiliary locks shall be as specified under hardware sets and conform to ANSI A156.5.

2.5   ARMOR PLATES, KICK PLATES, MOP PLATES AND DOOR EDGING

A.	Conform to ANSI Standard A156.6.

B.	Provide protective plates and door edging as specified below:

1.	Kick plates, mop plates and armor plates of stainless steel, Type J100 series.

2.	Provide Stainless Steel kick plates and mop plates at all locations where specified. Kick plates shall be 254 mm (10 inches) high. Mop plates shall be 152 mm (6 inches) high.  Both kick and mop plates shall be minimum 1.27 mm (0.050 inches) thick.  Provide kick and mop plates beveled on all 4 edges (B4E).  On push side of doors where jamb stop extends to floor, make kick plates 38 mm (1-1/2 inches) less than width of door, except pairs of metal doors which shall have plates 25 mm (1 inch) less than width of each door. Extend all other kick and mop plates to within 6 mm (1/4 inch) of each edge of doors. Kick and mop plates shall butt astragals. For jamb stop requirements, see specification sections pertaining to door frames.

3.	Kick plates and/or mop plates are not required on following door sides:

a.	Armor plate side of doors;

b.	Exterior side of exterior doors;

c.	Closet side of closet doors;

d.	Both sides of aluminum entrance doors.

4.	Armor plates for doors are listed under Article "Hardware Sets". Armor plates shall be thickness as noted in the hardware set, 875 mm (35 inches) high and 38 mm (1-1/2 inches) less than width of doors, except on pairs of metal doors. Provide armor plates beveled on all 4 edges (B4E).  Plates on pairs of metal doors shall be 25 mm (1 inch) less than width of each door. Where top of intermediate rail of door is less than 875 mm (35 inches) from door bottom, extend armor plates to within 13 mm (1/2 inch) of top of intermediate rail. On doors equipped with panic devices, extend armor plates to within 13 mm (1/2 inch) of panic bolt push bar.

5.	Where louver or grille occurs in lower portion of doors, substitute stretcher plate and kick plate in place of armor plate. Size of stretcher plate and kick plate shall be 254 mm (10 inches) high.

6.	Provide stainless steel edge guards where so specified at wood doors. Provide mortised type instead of surface type except where door construction and/or ratings will not allow.  Provide edge guards of bevel and thickness to match wood door.  Provide edge guards with factory cut-outs for door hardware that must be installed through or extend through the edge guard.  Provide full-height edge guards except where door rating does not allow; in such cases, provide edge guards to height of bottom of typical lockset armor front.  Forward edge guards to wood door manufacturer for factory installation on doors.

2.7   EXIT DEVICES

A.	Conform to ANSI Standard A156.3. Exit devices shall be Grade 1; type and function are specified in hardware sets. Provide flush with finished floor strikes for vertical rod exit devices in interior of building. Trim shall have cast satin stainless steel lever handles of design similar to locksets, unless otherwise specified. Provide key cylinders for keyed operating trim and, where specified, cylinder dogging.

B.	Surface vertical rod panics shall only be provided less bottom rod; provide fire pins as required by exit device and door fire labels.  Do not provide surface vertical rod panics at exterior doors.

C.	Concealed vertical rod panics shall be provided less bottom rod at interior doors, unless lockable or otherwise specified; provide fire pins as required by exit device and door fire labels.  Where concealed vertical rod panics are specified at exterior doors, provide with both top and bottom rods.

D.	Where removable mullions are specified at pairs with rim panic devices, provide mullion with key-removable feature.

E.	At non-rated openings with panic hardware, provide panic hardware with key cylinder dogging feature.

F.	Exit devices for fire doors shall comply with Underwriters Laboratories, Inc., requirements for Fire Exit Hardware. Submit proof of compliance.

2.8   THRESHOLDS

A.	Conform to ANSI A156.21, mill finish extruded aluminum, except as otherwise specified. In existing construction, thresholds shall be installed in a bed of sealant with ¼-20 stainless steel machine screws and expansion shields. In new construction, embed aluminum anchors coated with epoxy in concrete to secure thresholds. Furnish thresholds for the full width of the openings.

B.	For thresholds at elevators entrances see other sections of specifications.

C.	At exterior doors and any interior doors exposed to moisture, provide threshold with non-slip abrasive finish.

D.	Provide with miter returns where threshold extends more than 12 mm (0.5 inch) from fame face.

2.9   WEATHERSTRIPS (For Exterior Doors)

A.	Conform to ANSI A156.22. Air leakage shall not to exceed 0.50 CFM per foot of crack length (0.000774m3/s/m).

2.10 MISCELLANEOUS HARDWARE

A.	Mutes: Conform to ANSI A156.16. Provide door mutes or door silencers Type L03011 or L03021, depending on frame material, of white or light gray color, on each steel or wood door frame, except at fire-rated frames, lead-lined frames and frames for sound-resistant, lightproof and electromagnetically shielded doors. Furnish 3 mutes for single doors and 2 mutes for each pair of doors, except double-acting doors. Provide 4 mutes or silencers for frames for each Dutch type door. Provide 2 mutes for each edge of sliding door which would contact door frame.

7.	Roof Access and Scuttles: Engineer's set.

2.11  FINISHES

A.	Exposed surfaces of hardware shall have ANSI A156.18, finishes as specified below. Finishes on all hinges, pivots, closers, thresholds, etc., shall be as specified below under "Miscellaneous Finishes." For field painting (final coat) of ferrous hardware, see Section 09 91 00, PAINTING.

B.	626 or 630: All surfaces on exterior and interior of buildings, except where other finishes are specified.

C.	Miscellaneous Finishes:

1.	Hinges --exterior doors: 626 or 630.

2.	Hinges --interior doors: 652 or 630.

3.	Pivots: Match door trim.

4.	Door Closers: Factory applied paint finish. Dull or Satin Aluminum color.

5.	Thresholds: Mill finish aluminum.

6.	Cover plates for floor hinges and pivots: 630.

7.	Other primed steel hardware: 600.

D.	Hardware Finishes for Existing Buildings: U.S. Standard finishes shall match finishes of hardware in (similar) existing spaces except where otherwise specified.

E.	Special Finish: Exposed surfaces of hardware for dark bronze anodized aluminum doors shall have oxidized oil rubbed bronze finish (dark bronze) finish on door closers shall closely match doors.

F.	Anti-microbial Coating: All hand-operated hardware (levers, pulls, push bars, push plates, paddles, and panic bars) shall be provided with an anti-microbial/anti-fungal coating that has passed ASTM E2180 tests. Coating to consist of ionic silver (Ag+).  Silver ions surround bacterial cells, inhibiting growth of bacteria, mold, and mildew by blockading food and respiration supplies.

2.31 BASE METALS

A.	Apply specified U.S. Standard finishes on different base metals as following:

| Finish | Base Metal |
| --- | --- |
| 652 | Steel |
| 626 | Brass or bronze |
| 630 | Stainless steel |

PART 3 - EXECUTION

3.1 HARDWARE HEIGHTS

A.	For existing buildings locate hardware on doors at heights to match existing hardware. The Contractor shall visit the site, verify location of existing hardware and submit locations to VA C.O.R. for approval.

A.	For new addition locate hardware on doors at heights specified below, with all hand-operated hardware centered within 864 mm (34 inches) to 1200 mm (48 inches), unless otherwise noted:

B.	Hardware Heights from Finished Floor:

1.	Exit devices centerline of strike (where applicable) 1024 mm (40-5/16 inches).

2.	Locksets and latch sets centerline of strike 1024 mm (40-5/16 inches).

3.	Deadlocks centerline of strike 1219 mm (48 inches).

4.	Locate other hardware at standard commercial heights. Locate push and pull plates to prevent conflict with other hardware.

3.2 INSTALLATION

A.	Closer devices, including those with hold-open features, shall be equipped and mounted to provide maximum door opening permitted by building construction or equipment. Closers shall be mounted on side of door inside rooms, inside stairs, and away from corridors // except security bedroom, bathroom and anteroom doors which shall have closer installed parallel arm on exterior side of doors. //. At exterior doors, closers shall be mounted on interior side. Where closers are mounted on doors they shall be mounted with sex nuts and bolts; foot shall be fastened to frame with machine screws.

B.	Hinge Size Requirements:

| Door Thickness | Door Width | Hinge Height |
| --- | --- | --- |
| 45 mm (1-3/4 inch) | 900 mm (3 feet) and less | 113 mm (4-1/2 inches) |
| 45 mm (1-3/4 inch) | Over 900 mm (3 feet) but not more than 1200 mm (4 feet) | 125 mm (5 inches) |
| 35 mm (1-3/8 inch) (hollow core wood doors) | Not over 1200 mm (4 feet) | 113 mm (4-1/2 inches) |

C.	Hinge leaves shall be sufficiently wide to allow doors to swing clear of door frame trim and surrounding conditions.

D.	Where new hinges are specified for new doors in existing frames or existing doors in new frames, sizes of new hinges shall match sizes of existing hinges; or, contractor may reuse existing hinges provided hinges are restored to satisfactory operating condition as approved by C.O.R. Existing hinges shall not be reused on door openings having new doors and new frames. Coordinate preparation for hinge cut-outs and screw-hole locations on doors and frames.

E.	Hinges Required Per Door:

| Doors 1500 mm (5 ft) or less in height | 2 butts |
| --- | --- |
| Doors over 1500 mm (5 ft) high and not over 2280 mm (7 ft 6 in) high | 3 butts |
| Doors over 2280 mm (7 feet 6 inches) high | 4 butts |
| Dutch type doors | 4 butts |
| Doors with spring hinges 1370 mm (4 feet 6 inches) high or less | 2 butts |
| Doors with spring hinges over 1370 mm (4 feet 6 inches) | 3 butts |

F.	Fastenings: Suitable size and type and shall harmonize with hardware as to material and finish. Provide machine screws and lead expansion shields to secure hardware to concrete, ceramic or quarry floor tile, or solid masonry. Fiber or rawl plugs and adhesives are not permitted. All fastenings exposed to weather shall be of nonferrous metal.

G.	After locks have been installed; show in presence of Resident Engineer that keys operate their respective locks in accordance with keying requirements. (All keys, Master Key level and above shall be sent Registered Mail to the Medical Center Director along with the bitting list. Also a copy of the invoice shall be sent to the Resident Engineer for his records.) Installation of locks which do not meet specified keying requirements shall be considered sufficient justification for rejection and replacement of all locks installed on project.

3.3 FINAL INSPECTION

A.	Installer to provide letter to VA Resident/Project Engineer that upon completion, installer has visited the Project and has accomplished the following:

1.	Re-adjust hardware.

2.	Evaluate maintenance procedures and recommend changes or additions, and instruct VA personnel.

3.	Identify items that have deteriorated or failed.

4.	Submit written report identifying problems.

3.4 DEMONSTRATION

A.	Demonstrate efficacy of mechanical hardware and electrical, and electronic hardware systems, including adjustment and maintenance procedures, to satisfaction of C.O.R and VA Locksmith.

3.5 HARDWARE SETS

A.	Following sets of hardware correspond to hardware symbols shown on drawings. Only those hardware sets that are shown on drawings will be required. Disregard hardware sets listed in specifications but not shown on drawings.

B.	Hardware Consultant working on a project will be responsible for providing additional information regarding these hardware sets. The numbers shown in the following sets come from BHMA standards.

INTERIOR SINGLE DOORS

HW-1

Each Door to Have:							RATED/NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Keyed Lock				F04

(Corbin Russwin ML 2059-LWN-626-(RH/LH to suit location)–M19V-Occupancy Indicator + CLS6 Small IC 6P Less Core)

1	Closer				C02011/C02021 (Sargent 1431 Series)

1	Kick Plate				J102

1	Mop Plate (@ Inswing Doors)	J103

1	Floor Stop				L02121 x 3 FASTENERS

1	Set Self-Adhesive Seals		R0Y154

HW-2

Each Door to Have:							NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Privacy Lock			F02

(Corbin Russwin ML 2068-LWN-626-(RH/LH to suit location)– CLS6 Small IC 6P Less Core)

1	SS Kick Plate			J102

1	SS Mop Plate(@ Inswing Doors) J103

1	Floor Stop				L02121 x3 Fasteners

3	Silencers				L03011

1  Auto Bottom Seal			ROY346 – HEAVY DUTY

HW-3

Each Door to Have:							NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Entrance Lock			F04

(Corbin Russwin ML 2051-LWN-626-(RH/LH to suit location)– CLS6 Small IC 6P Less Core)

2	SS Kick Plate			J102

1	Closer				C02011/C02021 (Sargent 1431 Series)

1	Overhead Stop			ASSA ABLOY OH100 SERIES

3	Silencers				L03011

HW-4

Each Door to Have:							NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Office Lock				F04

(Corbin Russwin ML 2053-LWN-626-(RH/LH to suit location)– CLS6 Small IC 6P Less Core)

1	Floor Stop				L02121 x 3 FASTENERS

1	SS Kick Plate			J102

1	SS Mop Plate(@ Inswing Doors)	J103

1	Coat Hook				L03121

1	Threshold				J32300 x 57 mm width (2-1/4 inches)

2	Sets Self-Adhesive Seals	R0Y154

HW-4A

Each Door to Have:							NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Office Lock				F04

(Corbin Russwin ML 2053-LWN-626-(RH/LH to suit location)– CLS6 Small IC 6P Less Core)

1	Overhead Stop			ASSA ABLOY OH100 SERIES

1	SS Kick Plate			J102

1	SS Mop Plate(@ Inswing Doors)	J103

1	Coat Hook				L03121

2	Sets Self-Adhesive Seals	R0Y154

HW-4B

Each Door to Have:							NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Office Lock				F04

(Corbin Russwin ML 2053-LWN-626-(RH/LH to suit location)– CLS6 Small IC 6P Less Core)

1	Floor Stop				L02121 x 3 FASTENERS

1	SS Kick Plate			J102

1	SS Mop Plate(@ Inswing Doors)	J103

1	Coat Hook				L03121

2	Sets Self-Adhesive Seals	R0Y154

HW-5

Each Door to Have:							NON-RATED/RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Storeroom Lock			F04

(Corbin Russwin ML 2059-LWN-626-(RH/LH to suit location)–CLS6 Small IC 6P Less Core)

2	SS Kick Plates			J102

1	Set Auto Flush Bolts		TYPE 25 LESS BOTTOM BOLT

1 SS Overlapping Astagral		R3A734 x THRU-BOLTS

2 Overhead Stops			C01541 ADJUSTABLEHW-5

HW-6

Each Door to Have:							RATED

Hinges				QUANTITY & TYPE AS REQUIRED

1	Storeroom Lock			F02

(Corbin Russwin ML 2059-LWN-626-(RH/LH to suit location)–CLS6 Small IC 6P Less Core)

1	Closer				C02011/C02021 (Sargent 1431 Series)

1	Overhead Stop (in Rms 10

and 16 only)		ASSA ABLOY OH100 SERIES

1	SS Kick Plate			J102

1	Floor Stop				L02121 x 3 FASTENERS

1	Threshold (in Rm 10 only)	J32300 x 57 mm width (2-1/4 inches)

1	Auto Door Bottom			R0Y346 – HEAVY DUTY

2	Sets Self-Adhesive Seals	R0Y154

EXTERIOR SINGLE DOORS

HW-7

Each Door to Have:							RATED/NON-RATED

Hinges				QUANTITY & TYPE AS REQUIRED

- EXIT Panic Device			F-4

(Von Duprin Allegion 98-L-F-626-06-CYL-SEC-SNB-HM-S (RH/LH to suit location) + CLS6 Small IC 6P Less Core+ 996L lever trim with 6 pin interchangeable core cylinder on exterior)

1  Closer				C02011/C02021 (Sargent 1431 Series)

1	Overhead Stop			ASSA ABLOY OH100 SERIES

2	Armor Plate				J102

1	Set Self-Adhesive Seals		R0Y154

1	Threshold				J32300 x 57 mm width (2-1/4 inches)

- - - E N D - - -