SECTION 21 13 13
WET-PIPE SPRINKLER SYSTEMS

# PART 1 - GENERAL

# 1.1 Description

A.	Modification of the existing sprinkler system as indicated on the drawings and as further required by these specifications.

# 1.2 RELATED WORK

A.	Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

B.	Section 07 84 00, FIRESTOPPING.

C.	Section 09 91 00, PAINTING.

# 1.3 Design Criteria

A.	Design Basis Information: Provide design, materials, equipment, installation, inspection, and testing of the automatic sprinkler system in accordance with the requirements of NFPA 13.

1.	Perform hydraulic calculations in accordance with NFPA 13 utilizing the Area/Density method. Do not restrict design area reductions permitted for using quick response sprinklers throughout by the required use of standard response sprinklers in the areas identified in this section.

2.	Sprinkler Protection: Sprinkler hazard classifications shall be in accordance with NFPA 13. The hazard classification examples of uses and conditions identified in the Annex of NFPA 13 shall be mandatory for areas not listed below. Request clarification from the Government for any hazard classification not identified.  To determining spacing and sizing, apply the following coverage classifications:

a.	Light Hazard Occupancies: Patient care, treatment, and customary access areas.

b.	Ordinary Hazard Group 1 Occupancies: Laboratories, Mechanical Equipment Rooms, Transformer Rooms, Electrical Switchgear Rooms, Electric Closets, and Repair Shops.

c.	Ordinary Hazard Group 2 Occupancies: Storage rooms, trash rooms, clean and soiled linen rooms, pharmacy and associated storage, laundry, kitchens, kitchen storage areas, retail stores, retail store storage rooms, storage areas, building management storage, boiler plants, energy centers, warehouse spaces, file storage areas for the entire area of the space up to 140 square meters (1500 square feet) and Supply Processing and Distribution (SPD).

3.	Hydraulic Calculations: Calculated demand including hose stream requirements shall fall no less than 10 percent below the available water supply curve.

# 1.4 submittals

A.	Submit as one package in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES. Prepare detailed working drawings that are signed by a NICET Level III or Level IV Sprinkler Technician or stamped by a Registered Professional Engineer licensed in the field of Fire Protection Engineering. As the Government review is for technical adequacy only, the installer remains responsible for correcting any conflicts with other trades and building construction that arise during installation. Partial submittals will not be accepted. Material submittals shall be approved prior to the purchase or delivery to the job site. Suitably bind submittals in notebooks or binders and provide an index referencing the appropriate specification section. In addition to the hard copies, provide submittal items in Paragraphs 1.4(A)1 through 1.4(A)5 electronically in pdf format on a compact disc or as directed by the COR. Submittals shall include, but not be limited to, the following:

1.	Qualifications:

a.	Provide a copy of the installing contractors fire sprinkler and New York State contractor’s license.

b.	Provide a copy of the NICET certification for the NICET Level III or Level IV Sprinkler Technician who prepared and signed the detailed working drawings unless the drawings are stamped by a Registered Professional Engineer licensed in the field of Fire Protection Engineering.

c.	Provide documentation showing that the installer has been actively and successfully engaged in the installation of commercial automatic sprinkler systems for the past ten years.

2.	Drawings: Submit detailed 1:100 (1/8 inch) scale (minimum) working drawings conforming to the Plans and Calculations chapter of NFPA 13.  Drawings shall include graphical scales that allow the user to determine lengths when the drawings are reduced in size.  Include a plan showing the piping to the water supply test location.

3.	Manufacturer’s Data Sheets: Provide data sheets for all materials and equipment proposed for use on the system. Include listing information and installation instructions in data sheets. Where data sheets describe items in addition to those proposed to be used for the system, clearly identify the proposed items on the sheet.

4.	Calculation Sheets:

a.	Submit hydraulic calculation sheets in tabular form conforming to the requirements and recommendations of the Plans and Calculations chapter of NFPA 13.

5.	Final Document Submittals: Provide as-built drawings, testing and maintenance instructions in accordance with the requirements in Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES. In addition, submittals shall include, but not be limited to, the following:

a.	A complete set of as-built drawings showing the installed system with the specific interconnections between the system switches and the fire alarm equipment.  Provide a complete set in the formats as follows.  Submit items 2 and 3 below on a compact disc or as directed by the COR.

1)	One full size (or size as directed by the COR) printed copy.

2)	One complete set in electronic pdf format.

3)	One complete set in latest version of AutoCAD format as directed by the COR.

b.	Material and Testing Certificate: Upon completion of the sprinkler system installation or any partial section of the system, including testing and flushing, provide a copy of a completed Material and Testing Certificate as indicated in NFPA 13. Certificates shall be provided to document all parts of the installation.

c.	One paper copy of the Material and Testing Certificates and the Operations and Maintenance Manuals above shall be provided in a binder.  In addition, these materials shall be provided in pdf format on a compact disc or as directed by the COR.

# 1.5 QUALITY ASSURANCE

A.	Installer Reliability: The installer shall possess a valid State of New York fire sprinkler contractor's license. The installer shall have been actively and successfully engaged in the installation of commercial automatic sprinkler systems for the past ten years.

B.	Materials and Equipment: All equipment and devices shall be of a make and type listed by UL or approved by FM, or other nationally recognized testing laboratory for the specific purpose for which it is used. All materials, devices, and equipment shall be approved by the VA. All materials and equipment shall be free from defect.  All materials and equipment shall be new unless specifically indicated otherwise on the contract drawings.

# 1.6 APPLICABLE PUBLICATIONS

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.  The latest edition at the time of contract award shall be used for all publications referenced below

B.	National Fire Protection Association (NFPA):

13-13	Installation of Sprinkler Systems

25-14	Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems

101-15	Life Safety Code

170-15	Fire Safety Symbols

C.	Underwriters Laboratories, Inc. (UL):
Fire Protection Equipment Directory (2011)

D.	Factory Mutual Engineering Corporation (FM):

Approval Guide

# PART 2 - PRODUCTS

# 2.1 PIPING & FITTINGS

A.	Piping and fittings for sprinkler systems shall be in accordance with NFPA 13.

1.	Plain-end pipe fittings with locking lugs or shear bolts are not permitted.

2.	Piping sizes 50 mm (2 inches) and smaller shall be black steel Schedule 40 with threaded end connections.

3.	Piping sizes 65 mm (2 ½ inches) and larger shall be black steel Schedule 10 with grooved connections.  Grooves in Schedule 10 piping shall be rolled grooved only.

4.	Plastic piping shall not be permitted except for drain piping.

5.	Flexible sprinkler hose shall be FM Approved and limited to hose with threaded end fittings with a minimum inside diameter or 1-inch and a maximum length of 6-feet.

# 2.2 SPRINKLERS

A.	All sprinklers shall be FM approved quick response except “institutional” type sprinklers shall be permitted to be UL Listed quick response.  “Institutional” type sprinklers in Mental Health and Behavior Units shall be UL listed or FM approved quick response type. Maximum break away strength shall be certified by the manufacturer to be no more than 39 kPa (85 pounds). Provide FM approved quick response sprinklers in all areas, except that standard response sprinklers shall be provided in freezers, refrigerators, elevator hoistways, elevator machine rooms, and generator rooms.

B.	Temperature Ratings: In accordance with NFPA 13 except that sprinklers in elevator shafts and elevator machine rooms shall be no less than intermediate temperature rated and sprinklers in generator rooms shall be no less than high temperature rated.

C.	Provide sprinkler guards in accordance with NFPA 13 and when the elevation of the sprinkler head is less than 7 feet 6 inches above finished floor. The sprinkler guard shall be UL listed or FM approved for use with the corresponding sprinkler.

# 2.3 SPRINKLER CABINET

A.	Provide sprinkler cabinet with the required number of sprinkler heads of all ratings and types installed, and a sprinkler wrench for each type of sprinkler in accordance with NFPA 13. Locate adjacent to the riser.

B.	Provide a list of sprinklers installed in the property in the cabinet.  The list shall include the following:

1.	Manufacturer, model, orifice, deflector type, thermal sensitivity, and pressure for each type of sprinkler in the cabinet.

2.	General description of where each sprinkler is used.

3.	Quantity of each type present in the cabinet.

4.	Issue or revision date of list.

# 2.4 PIPE hangers, SUpports and Restraint of System PIping

Pipe hangers, supports, and restraint of system piping shall be in accordance with NFPA 13.

# 2.5 WALL, FLOOR AND CEILING PLATES

Provide chrome plated steel escutcheon plates.

# PART 3 - EXECUTION

# 3.1 INSTALLATION

A.	Installation shall be accomplished by the licensed contractor. Provide a qualified technician, experienced in the installation and operation of the type of system being installed, to supervise the installation and testing of the system.

B.	Installation of Piping: Accurately cut pipe to measurements established by the installer and work into place without springing or forcing. In any situation where bending of the pipe is required, use a standard pipe-bending template. Concealed piping in spaces that have finished ceilings. Where ceiling mounted equipment exists, such as in operating and radiology rooms, install sprinklers so as not to obstruct the movement or operation of the equipment. Sidewall heads may need to be utilized. In stairways, locate piping as near to the ceiling as possible to prevent tampering by unauthorized personnel and to provide a minimum headroom clearance of 2250 mm (seven feet six inches). Piping shall not obstruct the minimum means of egress clearances required by NFPA 101. Pipe hangers, supports, and restraint of system piping shall be installed accordance with NFPA 13.

C.	Welding: Conform to the requirements and recommendations of NFPA 13.

D.	Provide escutcheon plates for exposed piping passing through walls, floors or ceilings.

E.	Sleeves: Provide for pipes passing through masonry or concrete. Provide space between the pipe and the sleeve in accordance with NFPA 13. Seal this space with a UL Listed through penetration fire stop material in accordance with Section 07 84 00, FIRESTOPPING. Where core drilling is used in lieu of sleeves, also seal space. Seal penetrations of walls, floors and ceilings of other types of construction, in accordance with Section 07 84 00, FIRESTOPPING.

D.	Firestopping shall be provided for all penetrations of fire resistance rated construction. Firestopping shall comply with Section 07 84 00, FIRESTOPPING.

E.	Painting of Pipe: In finished areas where walls and ceilings have been painted, paint primed surfaces with two coats of paint to match adjacent surfaces, except paint valves and operating accessories with two coats of gloss red enamel.  Exercise care to avoid painting sprinklers.  Painting of sprinkler systems above suspended ceilings and in crawl spaces is not required.  Painting shall comply with Section 09 91 00, PAINTING.  Any painted sprinkler shall be replaced with a new sprinkler.

F.	Repairs: Repair damage to the building or equipment resulting from the installation of the sprinkler system by the installer at no additional expense to the Government.

G.	Interruption of Service: There shall be no interruption of the existing sprinkler protection, water, electric, or fire alarm services without prior permission of the Contracting Officer. Contractor shall develop an interim fire protection program where interruptions involve occupied spaces. Request in writing at least one week prior to the planned interruption.

H. Sprinkler heads shall be installed in accordance with manufacturer’s installation instructions and requirements.

3.2 INSPECTION AND TEST

A.	Preliminary Testing: Flush newly installed systems prior to performing hydrostatic tests in order to remove any debris which may have been left as well as ensuring piping is unobstructed. Hydrostatically test system, including the fire department connections, as specified in NFPA 13, in the presence of the Contracting Officers Representative (COR) or his designated representative. Test and flush underground water line prior to performing these hydrostatic tests.

B.	Final Inspection and Testing: Subject system to tests in accordance with NFPA 13, and when all necessary corrections have been accomplished, advise COR to schedule a final inspection and test. Connection to the fire alarm system shall have been in service for at least ten days prior to the final inspection, with adjustments made to prevent false alarms. Furnish all instruments, labor and materials required for the tests and provide the services of the installation foreman or other competent representative of the installer to perform the tests. Correct deficiencies and retest system as necessary, prior to the final acceptance. Include the operation of all features of the systems under normal operations in test

# 3.3 INSTRUCTIONS

Furnish the services of a competent instructor for not less than two hours for instructing personnel in the operation and maintenance of the system, on the dates requested by the COR.

- - - E N D - - -