SECTION 22 05 23

GENERAL-DUTY VALVES FOR PLUMBING PIPING

# PART 1 - GENERAL

# 1.1 DESCRIPTION

A.	This section describes the requirements for general-duty valves for domestic water and sewer systems.

B.	A complete listing of all acronyms and abbreviations are included in Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING.

# 1.2 RELATED WORK

A.	Section 01 00 00, GENERAL REQUIREMENTS.

B.	Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES.

C.	Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS.

D.	Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING.

# 1.3 APPLICABLE PUBLICATIONS

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B.	American Society of Mechanical Engineers (ASME):

A112.14.1-2003	Backwater Valves

C.	American Society of Sanitary Engineering (ASSE):

1001-2008	Performance Requirements for Atmospheric Type Vacuum Breakers

1003-2009	Performance Requirements for Water Pressure Reducing Valves for Domestic Water Distribution Systems

1011-2004	Performance Requirements for Hose Connection Vacuum Breakers

1013-2011	Performance Requirements for Reduced Pressure Principle Backflow Preventers and Reduced Pressure Principle Fire Protection Backflow Preventers

1015-2011	Performance Requirements for Double Check Backflow Prevention Assemblies and Double Check Fire Protection Backflow Prevention Assemblies

1017-2009	Performance Requirements for Temperature Actuated Mixing Valves for Hot Water Distribution Systems

1020-2004	Performance Requirements for Pressure Vacuum Breaker Assembly

1035-2008	Performance Requirements for Laboratory Faucet Backflow Preventers

1069-2005	Performance Requirements for Automatic Temperature Control Mixing Valves

1070-2004	Performance Requirements for Water Temperature Limiting Devices

1071-2012	Performance Requirements for Temperature Actuated Mixing Valves for Plumbed Emergency Equipment

D.	American Society for Testing and Materials (ASTM):

A126-2004(R2009)	Standard Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings

A276-2013a	Standard Specification for Stainless Steel Bars and Shapes

A536-1984(R2009)	Standard Specification for Ductile Iron Castings

B62-2009	Standard Specification for Composition Bronze or Ounce Metal Castings

B584-2013	Standard Specification for Copper Alloy Sand Castings for General Applications

E.	International Code Council (ICC):

IPC-2012	International Plumbing Code

F.	Manufacturers Standardization Society of the Valve and Fittings Industry, Inc. (MSS):

SP-25-2008	Standard Marking Systems for Valves, Fittings, Flanges and Unions

SP-67-2011	Butterfly Valves

SP-70-2011	Gray Iron Gate Valves, Flanged and Threaded Ends

SP-71-2011	Gray Iron Swing Check Valves, Flanged and Threaded Ends

SP-80-2013	Bronze Gate, Globe, Angle, and Check Valves

SP-85-2011	Gray Iron Globe & Angle Valves, Flanged and Threaded Ends

SP-110-2010	Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

G.	National Environmental Balancing Bureau (NEBB):

7th Edition 2005	Procedural Standards for Testing, Adjusting, Balancing of Environmental Systems

H.	NSF International (NSF):

61-2012	Drinking Water System Components – Health Effects

372-2011	Drinking Water System Components – Lead Content

I.	University of Southern California Foundation for Cross Connection Control and Hydraulic Research (USC FCCCHR):

9th Edition	Manual of Cross-Connection Control

# 1.4 SUBMITTALS

A.	Submittals, including number of required copies, shall be submitted in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES.

B.	Information and material submitted under this section shall be marked “SUBMITTED UNDER SECTION 22 05 23, GENERAL-DUTY VALVES FOR PLUMBING PIPING”, with applicable paragraph identification.

C.	Manufacturer's Literature and Data Including: Full item description and optional features and accessories. Include dimensions, weights, materials, applications, standard compliance, model numbers, size, and capacity.

1.	Ball Valves.

2.	Check Valves.

3.	Thermostatic Mixing Valves.

D.	Complete operating and maintenance manuals including wiring diagrams, technical data sheets and information for ordering replaceable parts:

1.	Include complete list indicating all components of the systems.

2.	Include complete diagrams of the internal wiring for each item of equipment.

3.	Diagrams shall have their terminals identified to facilitate installation, operation and maintenance.

4.	Piping diagrams of thermostatic mixing valves to be installed.

# 1.5 DELIVERY, STORAGE, AND HANDLING

A.	Valves shall be prepared for shipping as follows:

1.	Protect internal parts against rust and corrosion.

2.	Protect threads, flange faces, grooves, and weld ends.

3.	Set angle, gate, and globe valves closed to prevent rattling.

4.	Set ball and plug valves open to minimize exposure of functional surfaces.

5.	Set butterfly valves closed or slightly open.

6.	Block check valves in either closed or open position.

B.	Valves shall be prepared for storage as follows:

1.	Maintain valve end protection.

2.	Store valves indoors and maintain at higher than ambient dew point temperature.

C.	A sling shall be used for large valves. The sling shall be rigged to avoid damage to exposed parts. Hand wheels or stems shall not be used as lifting or rigging points.

# PART 2 - PRODUCTS

# 2.1 VALVES, GENERAL

A.	Asbestos packing and gaskets are prohibited.

B.	Bronze valves shall be made with dezincification resistant materials. Bronze valves made with copper alloy (brass) containing more than 15 percent zinc shall not be permitted.

C.	Valves in insulated piping shall have 50 mm or DN50 (2 inch) stem extensions and extended handles of non-thermal conductive material that allows operating the valve without breaking the vapor seal or disturbing the insulation. Memory stops shall be fully adjustable after insulation is applied.

D.	Exposed Valves over 65 mm or DN65 (2-1/2 inches) installed at an elevation over 3.6 m (12 feet) shall have a chain-wheel attachment to valve hand-wheel, stem, or other actuator.

E.	All valves used to supply potable water shall meet the requirements of NSF 61 and NSF 372.

F.	Bio-Based Materials: For products designated by the USDA’s Bio-Preferred Program, provide products that meet or exceed USDA recommendations for bio-based content, so long as products meet all performance requirements in this specifications section. For more information regarding the product categories covered by the Bio-Preferred Program, visit http://www.biopreferred.gov.

# 2.2 SHUT-OFF VALVES

A.	Cold, Hot and Re-circulating Hot Water:

1.	50 mm or DN50 (2 inches) and smaller: Ball, MSS SP-110, Ball valve shall be full port three piece or two piece with a union design with adjustable stem package. Threaded stem designs are not allowed. The ball valve shall have a SWP rating of 1035 kPa (150 psig) and a CWP rating of 4138 kPa (600 psig). The body material shall be Bronze ASTM B584, Alloy C844. The ends shall be non-lead solder.

# 2.3 CHECK VALVES

A.	75 mm or DN75 (3 inches) and smaller shall be Class 125, bronze swing check valves with non-metallic disc suitable for type of service. The check valve shall meet MSS SP-80 Type 4 standard. The check valve shall have a CWP rating of 1380 kPa (200 psig). The check valve shall have a Y pattern horizontal body design with bronze body material conforming to ASTM B62, solder joints, and PTFE or TFE disc.

B.	100 mm or DN100 (4 inches) and larger:

1.	Check valves shall be Class 125, iron swing check valve with lever and weight closure control. The check valve shall meet MSS SP-71 Type I standard. The check valve shall have a CWP rating of 1380 kPa (200 psig). The check valve shall have a clear or full waterway body design with gray iron body material conforming to ASTM A126, bolted bonnet, flanged ends, bronze trim.

2.	All check valves on the discharge side of submersible sump pumps shall have factory installed exterior level and weight with sufficient weight to prevent the check valve from hammering against the seat when the sump pump stops.

# 2.4 THERMOSTATIC MIXING VALVES

A.	Thermostatic Mixing Valves shall comply with the following general performance requirements:

1.	Shall meet ASSE requirements for water temperature control.

2.	The body shall be cast bronze or brass with corrosion resistant internal parts preventing scale and biofilm build-up. Provide chrome-plated finish in exposed areas.

3.	No special tool shall be required for temperature adjustment, maintenance, replacing parts and disinfecting operations.

4.	Valve shall be able to be placed in various positions without making temperature adjustment or reading difficult.

5.	Valve finish shall be chrome plated in exposed areas.

6.	Valve shall allow easy temperature adjustments to allow hot water circulation. Internal parts shall be able to withstand disinfecting operations of chemical and thermal treatment of water temperatures up to 82°C (180°F) for 30 minutes or 50 mg/L (50 ppm) chlorine residual concentration for 24 hours.

7.	Parts shall be easily removed or replaced without dismantling the valves, for easy scale removal and disinfecting of parts.

8.	Valve shall have a manual adjustable temperature control with locking mechanism to prevent tampering by end user. Outlet temperature shall be visible to ensure outlet temperature does not exceed specified limits, particularly after thermal eradication procedures.

9.	Provide mixing valves with integral check valves with screens and stop valves.

B.	Water Temperature Limiting Devices:

1.	Application: Single plumbing fixture point-of-use such as sinks or lavatories.

2.	Standard: ASSE 1070.

3.	Pressure Rating: 861 kPa (125 psig).

4.	Type: Thermostatically controlled water mixing valve set at 43 degrees C (110 degrees F).

5.	Connections: Threaded union, compression or soldered inlets and outlet.

6.	Upon cold water supply failure the hot water flow shall automatically be shut off.

# PART 3 - EXECUTION

# 3.1 EXAMINATION

A.	Valve interior shall be examined for cleanliness, freedom from foreign matter, and corrosion. Special packing materials shall be removed, such as blocks, used to prevent disc movement during shipping and handling.

B.	Valves shall be operated in positions from fully open to fully closed. Guides and seats shall be examined and made accessible by such operations.

C.	Threads on valve and mating pipe shall be examined for form and cleanliness.

D.	Mating flange faces shall be examined for conditions that might cause leakage. Bolting shall be checked for proper size, length, and material. Gaskets shall be verified for proper size and that its material composition is suitable for service and free from defects and damage.

E.	Do not attempt to repair defective valves; replace with new valves.

# 3.2 INSTALLATION

A.	Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

B.	Valves shall be located for easy access and shall be provide with separate support. Valves shall be accessible with access doors when installed inside partitions or above hard ceilings.

C.	Valves shall be installed in horizontal piping with stem at or above center of pipe.

D.	Valves shall be installed in a position to allow full stem movement.

E.	Check valves shall be installed for proper direction of flow and as follows:

1.	Swing Check Valves: In horizontal position with hinge pin level and on top of valve.

F.	If an installation is unsatisfactory to the COR, the Contractor shall correct the installation at no cost to the Government.

# 3.3 ADJUSTING

A.	Valve packing shall be adjusted or replaced after piping systems have been tested and put into service but before final adjusting and balancing. Valves shall be replaced if persistent leaking occurs.

B.	Set field-adjustable flow set points of balancing valves and record data. Ensure recorded data represents actual measured or observed conditions. Permanently mark settings of valves and other adjustment devices allowing settings to be restored. Set and lock memory stops. After adjustment, take measurements to verify balance has not been disrupted or that such disruption has been rectified.

C.	Set field-adjustable temperature set points of temperature-actuated water mixing valves.

# 3.4 COMMISSIONING

A.	NA

- - E N D - - -