# SECTION 22 14 00

# FACILITY STORM DRAINAGE

# PART 1 - GENERAL

## 1.1 DESCRIPTION

A.	This section describes the requirements for storm drainage systems, including piping and all necessary accessories as designated in this section.

B.	A complete listing of all acronyms and abbreviations are included in Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING.

## 1.2 RELATED WORK

A.	Section 01 00 00, GENERAL REQUIREMENTS.

B.	Section 07 84 00, FIRESTOPPING: Penetrations in rated enclosures.

C.	Section 07 92 00, JOINT SEALANTS.

D.	Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING: Pipe Hangers and Supports, Materials Identification.

## 1.3 APPLICABLE PUBLICATIONS

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B.	American Society of Mechanical Engineers (ASME):

A112.6.4-2003 (R2012) 	Roof, Deck, and Balcony Drains

A13.1-2007 (R2013)	Scheme for Identification of Piping Systems

B1.20.1-2013	Pipe Threads, General Purpose, Inch

B16.3-2011	Malleable Iron Threaded Fittings: Classes 150 and 300

B16.9-2012	Factory-Made Wrought Buttwelding Fittings

B16.11-2011	Forged Fittings, Socket-Welding and Threaded

B16.12-2009 (R2014)	Cast Iron Threaded Drainage Fittings

B16.15-2013	Cast Copper Alloy Threaded Fittings: Classes 125 and 250

B16.18-2012	Cast Copper Alloy Solder-Joint Pressure Fittings

B16.22-2013	Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings

B16.23-2011	Cast Copper Alloy Solder Joint Drainage Fittings - DWV

B16.29-2012	Wrought Copper and Wrought Copper Alloy Solder-Joint Drainage Fittings – DWV

C.	American Society of Sanitary Engineering (ASSE)

1079-2012	Performance Requirements for Dielectric Pipe Unions

D.	American Society for Testing and Materials (ASTM):

A47/A47M-1999 (R2014)	Standard Specification for Ferritic Malleable Iron Castings

A53/A53M-2012	Standard Specification for Pipe, Steel, Black And Hot-Dipped, Zinc-coated Welded and Seamless

A74-2013a	Standard Specification for Cast Iron Soil Pipe and Fittings

A183-2014	Standard Specification for Carbon Steel Track Bolts and Nuts

A312/A312M-2015	Standard Specification for Seamless, Welded, and Heavily Cold Worked Austenitic Stainless Steel Pipes

A536-1984(R2014)	Standard Specification for Ductile Iron Castings

A733-2013	Standard Specification for Welded and Seamless Carbon Steel and Austenitic Stainless Steel Pipe Nipples

A888-2013a	Standard Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent Piping Applications

B32-2008 (R2014)	Standard Specification for Solder Metal

B61-2008 (R2013)	Standard Specification for Steam or Valve Bronze Castings

B62-2009	Standard Specification for Composition Bronze or Ounce Metal Castings

B75/B75M-2011	Standard Specification for Seamless Copper Tube

B88-2014	Standard Specification for Seamless Copper Water Tube

B306-2013	Standard Specification for Copper Drainage Tube (DWV)

B584-2014	Standard Specification for Copper Alloy Sand Castings for General Applications

B687-1999 (R2011)	Standard Specification for Brass, Copper, and Chromium-Plated Pipe Nipples

B828-2002 (R2010)	Standard Practice for Making Capillary Joints by Soldering of Copper and Copper Alloy Tube and Fittings

B813-2010	Standard Specification for Liquid and Paste Fluxes for Soldering of Copper and Copper Alloy Tube

C564-2014	Standard Specification for Rubber Gaskets for Cast Iron Soil Pipe and Fittings

C1173-2010 (R2014)	Standard Specification for Flexible Transition Couplings for Underground Piping Systems

D1785-2012	Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80 and 120

D2000-2012	Standard Classification System for Rubber Products in Automotive Applications

D2321-2014e1	Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications

D2564-2012	Standard Specification for Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Piping Systems

D2665-2014	Standard Specification for Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings

D2855-1996 (R2010)	Standard Practice for Making Solvent-Cemented Joints with Poly (Vinyl Chloride) (PVC) Pipe and Fittings

D4101-2014	Standard Specification for Polypropylene Injection and Extrusion Materials

D5926-2011	Standard for Poly (Vinyl Chloride) (PVC) Gaskets for Drain, Waste, and Vent (DWV), Sewer, Sanitary, and Storm Plumbing Systems

F477-2014	Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

F656-2010	Standard Specification for Primers for Use in Solvent Cement Joints of Poly (Vinyl Chloride) (PVC) Plastic Pipe and Fittings

F1545-2015	Standard Specification for Plastic-Lined Ferrous Metal Pipe, Fittings, and Flanges

E.	American Welding Society (AWS):

A5.8M/A5.8 AMD1-2011	Specification for Filler Metals for Brazing and Braze Welding

F.	Copper Development Association (CDA):

A4015-2011	Copper Tube Handbook

G.	Cast Iron Soil Pipe Institute (CISPI):

301-2012	Standard Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent Piping Applications

310-2012	Standard Specification for Coupling for Use in Connection with Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent Piping Applications

H.	International Code Council (ICC):

IPC-2012	International Plumbing Code

I.	Manufacturers Standardization Society of the Valve and Fittings Industry, Inc. (MSS):

SP-72-2010a	Ball Valves with Flanged or Butt-Welding Ends for General Service

SP-110-2010	Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

## 1.4 SUBMITTALS

A.	Submittals, including number of required copies, shall be submitted in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

B.	Information and material submitted under this section shall be marked “SUBMITTED UNDER SECTION 22 14 00, FACILITY STORM DRAINAGE”, with applicable paragraph identification.

C.	Manufacturer's Literature and Data including: Full item description and optional features and accessories. Include dimensions, weights, materials, applications, standard compliance, model numbers, size, and capacity.

1.	Pipe and Fittings

2.	Roof Drains.

D.	Detailed shop drawing of clamping device and extensions when required in connection with the waterproofing membrane.

## 1.5 QUALITY ASSURANCE

A.	Bio-Based Materials: For products designated by the USDA’s Bio-Preferred Program, provide products that meet or exceed USDA recommendations for bio-based content, so long as products meet all performance requirements in this specifications section. For more information regarding the product categories covered by the Bio-Preferred Program, visit http://www.biopreferred.gov.

# PART 2 - PRODUCTS

## 2.1 STORM WATER DRAIN PIPING

A.	Cast Iron Storm Pipe and Fittings:

1.	Cast iron storm pipe and fittings shall be used for the following applications:

a.	Pipe buried in or in contact with earth.

b.	Extension of pipe to a distance of approximately 1500 mm (5 feet) outside of building walls.

c.	Interior storm piping above grade.

d.	All mechanical equipment rooms or other areas containing mechanical air handling equipment.

2.	The cast iron storm pipe shall be bell and spigot, or hubless (plain end or no-hub) as required by selected jointing method.

3.	The material for all pipe and fittings shall be cast iron soil pipe and fittings and shall conform to the requirements of CISPI 301, ASTM A888, or ASTM A74.

4.	Joints for hubless pipe and fittings shall conform to the manufacturer’s installation instructions. Couplings for hubless joints shall conform to CISPI 310. Joints for hub and spigot pipe shall be installed with compression gaskets conforming to the requirements of ASTM C564.

## 2.2 ROOF DRAINS AND CONNECTIONS

A.	Roof Drains: Roof Drains (RD) shall be cast iron with clamping device for making watertight connection and shall conform with ASME A112.6.4. Free openings through strainer shall be twice area of drain outlet. For roof drains not installed in connection with a waterproof membrane, a soft copper membrane shall be provided 300 mm (12 inches) in diameter greater than outside diameter of drain collar. An integral gravel stop shall be provided for drains installed on roofs having built up roofing covered with gravel or slag. Integral no-hub, soil pipe gasket or threaded outlet connection shall be provided.

1.	Flat Roofs: The roof drain shall have a beehive or dome shaped strainer with integral flange not less than 300 mm (12 inches) in diameter. For an insulated roof, a roof drain with an adjustable drainage collar shall be provided, which can be raised or lowered to meet required insulation heights, sump receiver and deck clamp. The bottom section shall serve as roof drain during construction before insulation is installed.

2.	Protective Roof Membrane Insulation Assembly: The roof drain shall have a perforated stainless steel extension filter, non-puncturing clamp ring, large sump with extra wide roof flange and deck clamp.

a.	Non pedestrian Roofs: The roof drain shall have large polypropylene or aluminum locking dome.

b.	Pedestrian Roof: The roof drain shall have a bronze promenade top 356 mm (14 inches) square, set in square secured frame support collar.

3.	Roof drains in areas subject to freezing shall have heat tape and shall be insulated.

# PART 3 - EXECUTION

## 3.1 PIPE INSTALLATION

A.	The pipe installation shall comply with the requirements of the IPC and these specifications.

B.	Branch piping shall be installed from the piping system and connect to all drains and outlets.

C.	Pipe shall be round and straight. Cutting shall be done with proper tools. Pipe, except for glass, shall be reamed to remove burrs and a clean smooth finish restored to full pipe inside diameter.

D.	All pipe runs shall be laid out to avoid interference with other work/trades.

E.	The piping shall be installed above accessible ceilings to allow for ceiling panel removal.

F.	Unless otherwise stated on the documents, minimum horizontal slope shall be one inch for every 2.44 m (8 feet) (1 percent slope) of pipe length.

G.	The piping shall be installed free of sags and bends.

H.	Seismic restraint shall be installed where required by code.

I.	Changes in direction for storm drainage piping shall be made using appropriate branches, bends and long sweep bends. Sanitary tees and short sweep ¼ bends may be used on vertical stacks if change in direction of flow is from horizontal to vertical. Long turn double wye branch and 1/8 bend fittings shall be used if two drains are installed back to back or side by side with common drain pipe. Do not change direction of flow more than 90 degrees. Proper size of standard increaser and reducers shall be used if pipes of different sizes are connected. Reducing size of drainage piping in direction of flow is prohibited.

J.	Cast iron piping shall be installed according to CISPI’s “Cast Iron Soil Pipe and Fittings Handbook,” Chapter IV, “Installation of Cast Iron Soil Pipe and Fittings”

## 3.2 JOINT CONSTRUCTION

A.	Hub and spigot, cast iron piping with gasket joints shall be joined in accordance with CISPI’s “Cast Iron Soil Pipe and Fittings Handbook” for compression joints.

B.	Hub and spigot, cast iron piping with calked joints shall be joined in accordance with CISPI’s “Cast Iron Soil Pipe and Fittings Handbook” for lead and oakum calked joints.

C.	Hubless, cast iron piping shall be joined in accordance with CISPI’s “Cast Iron Soil Pipe and Fittings Handbook” for hubless piping coupling joints.

D.	For threaded joints, thread pipe with tapered pipe threads according to ASME B1.20.1. The threads shall be cut full and clean using sharp disc cutters. Threaded pipe ends shall be reamed to remove burrs and restored to full pipe inside diameter. Pipe fittings and valves shall be joined as follows:

1.	Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is required by the pipe service

2.	Pipe sections with damaged threads shall be replaced with new undamaged sections of pipe at no additional time or cost to Government.

## 3.3 SPECIALTY PIPE FITTINGS

A.	Transition coupling shall be installed at pipe joints with small differences in pipe outside diameters.

B.	Dielectric fittings shall be installed at connections of dissimilar metal piping and tubing.

## 3.4 PIPE HANGERS, SUPPORTS AND ACCESSORIES

A.	All piping shall be supported according to the IPC, Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING, and these specifications.

B.	Hangers, supports, rods, inserts and accessories used for Pipe supports shall be shop coated with zinc Chromate primer paint. Electroplated copper hanger rods, hangers and accessories may be used with copper tubing.

C.	Horizontal piping and tubing shall be supported within 300 mm (12 inches) of each fitting or coupling.

D.	Horizontal cast iron piping shall be supported with the following maximum horizontal spacing and minimum hanger rod diameters:

1.	NPS 1-1/2 to NPS 2 (DN 40 to DN 50): 1500 mm (60 inches) with 10 mm (3/8 inch) rod.

2.	NPS 3 (DN 80): 1500 mm (60 inches) with 15 mm (1/2 inch) rod.

3.	NPS 4 to NPS 5 (DN 100 to DN 125): 1500 mm (60 inches) with 18 mm (5/8 inch) rod.

4.	NPS 6 to NPS 8 (DN 150 to DN 200): 1500 mm (60 inches) with 20 mm (3/4 inch) rod.

5.	NPS 10 to NPS 12 (DN 250 to DN 300): 1500 mm (60 inches) with 23 mm (7/8 inch) rod.

E.	The maximum support spacing for horizontal plastic shall be 1.22 m (4 feet).

F.	Vertical piping and tubing shall be supported at the base, at each floor, and at intervals no greater than 4.6 m (15 feet).

G.	In addition to the requirements in Section 22 05 11, COMMON WORK RESULTS FOR PLUMBING, floor, wall and ceiling plates shall have the following characteristics:

1.	Solid or split unplated cast iron.

2.	All plates shall be provided with set screws.

3.	Height adjustable clevis type pipe hangers.

4.	Adjustable Floor Rests and Base Flanges shall be steel.

5.	Hanger Rods shall be low carbon steel, fully threaded or threaded at each end with two removable nuts at each end for positioning rod and hanger and locking each in place.

6.	Riser Clamps shall be malleable iron or steel.

7.	Roller shall be cast iron.

8.	Hangers and supports utilized with insulated pipe and tubing shall have 180 degree (minimum) metal protection shield centered on and welded to the hanger and support. The shield shall be 100 mm (4 inches) in length and be 1.6 mm (16 gage) steel. The shield shall be sized for the insulation.

H.	Miscellaneous materials shall be provided as specified, required, directed or as noted on the drawings for proper installation of hangers, supports and accessories. If the vertical distance exceeds 6.1 m (20 feet) for cast iron pipe additional support shall be provided in the center of that span. All necessary auxiliary steel shall be provided to provide that support.

I.	Cast escutcheon with set screw shall be installed at each wall, floor and ceiling penetration in exposed finished locations and within cabinets and millwork.

J.	Penetrations:

1.	Fire Stopping: Where pipes pass through fire partitions, fire walls, smoke partitions, or floors, a fire stop shall be installed that provides an effective barrier against the spread of fire, smoke and gases as specified in Section 07 84 00, FIRESTOPPING. Clearances between raceways and openings shall be completely filled and sealed with the fire stopping materials.

2.	Water proofing: At floor penetrations, Clearances around the pipe shall be completely sealed and made watertight with sealant as specified in Section 07 92 00, JOINT SEALANTS. Bio-based materials shall be utilized when possible.

3.5 INSULATION

A.	Insulate horizontal sections and 600 mm (2 feet) past changes of direction to vertical sections for interior section of roof drains. Install insulation in accordance with the requirements of Section 22 07 11, PLUMBING INSULATION.

- - - E N D - - -