SECTION 23 23 00
REFRIGERANT PIPING

PART 1 - GENERAL

1.1 DESCRIPTION

A.	Field refrigerant piping for direct expansion HVAC systems.

B.	Refrigerant piping shall be sized, selected, and designed either by the equipment manufacturer or in strict accordance with the manufacturer’s published instructions.  The schematic piping diagram shall show all accessories such as, stop valves, level indicators, liquid receivers, oil separator, gauges, thermostatic expansion valves, solenoid valves, moisture separators and driers to make a complete installation.

C.	Definitions:

1.	Refrigerating system: Combination of interconnected refrigerant-containing parts constituting one closed refrigeration circuit in which a refrigerant is circulated for the purpose of extracting heat.

a.	Low side means the parts of a refrigerating system subjected to evaporator pressure.

b.	High side means the parts of a refrigerating system subjected to condenser pressure.

2.	Brazed joint: A gas-tight joint obtained by the joining of metal parts with alloys which melt at temperatures higher than 449 degrees C (840 degrees F) but less than the melting temperatures of the joined parts.

1.2 RELATED WORK

A.	Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES.

B.	Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

C.	Section 23 07 11, HVAC, and BOILER PLANT INSULATION.

1.3 QUALITY ASSURANCE

A.	Refer to specification Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

B.	Comply with ASHRAE Standard 15, Safety Code for Mechanical Refrigeration. The application of this Code is intended to assure the safe design, construction, installation, operation, and inspection of every refrigerating system employing a fluid which normally is vaporized and liquefied in its refrigerating cycle.

C.	Comply with ASME B31.5: Refrigerant Piping and Heat Transfer Components.

D.	Products shall comply with UL 207 "Refrigerant–Containing Components and Accessories, "Nonelectrical"; or UL 429 "Electrical Operated Valves."

1.4 SUBMITTALS

A.	Submit in accordance with specification Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES.

B.	Shop Drawings:

1.	Complete information for components noted, including valves and refrigerant piping accessories, clearly presented, shall be included to determine compliance with drawings and specifications for components noted below:

a.	Tubing and fittings

b.	Valves

c.	Strainers

d.	Moisture-liquid indicators

e.	Filter-driers

f.	Flexible metal hose

g.	Liquid-suction interchanges

h.	Oil separators (when specified)

i.	Gages

j.	Pipe and equipment supports

k.	Refrigerant and oil

l.	Pipe/conduit roof penetration cover

m.	Soldering and brazing materials

2.	Layout of refrigerant piping and accessories, including flow capacities, valves locations, and oil traps slopes of horizontal runs, floor/wall penetrations, and equipment connection details.

C.	Certification: Copies of certificates for welding procedure, performance qualification record and list of welders' names and symbols.

D.	Design Manual: Furnish two copies of design manual of refrigerant valves and accessories.

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B.	Air Conditioning, Heating, and Refrigeration Institute (ARI/AHRI):

495-//2005//	Standard for Refrigerant Liquid Receivers

730-//2013//	Flow Capacity Rating of Suction-Line Filters and Suction-Line Filter-Driers

750-//2016//	Thermostatic Refrigerant Expansion Valves

760-//202014//	Performance Rating of Solenoid Valves for Use with Volatile Refrigerants

C.	American Society of Heating Refrigerating and Air Conditioning Engineers (ASHRAE):

15-//2019//	Safety Standard for Refrigeration Systems (ANSI)

17-//2008//	Method of Testing Capacity of Thermostatic Refrigerant Expansion Valves (ANSI)

63.1-//2001//	Method of Testing Liquid Line Refrigerant Driers (ANSI)

63.2-//2010//	Method of Testing Liquid Line Filter Drier Filtration Capability (ANSI)

D.	American National Standards Institute (ANSI):

A13.1-//2015//Scheme for Identification of Piping Systems

Z535.1-//2017//	Safety Color Code

E.	American Society of Mechanical Engineers (ASME):

B16.22-//2018// Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings (ANSI)

B16.24-//20016//Cast Copper Alloy Pipe Flanges and Flanged Fittings, Class 150, 300, 400, 600, 900, 1500 and 2500 (ANSI)

B31.5-//2013// Refrigeration Piping and Heat Transfer Components (ANSI)

B40.100-//2013//	Pressure Gauges and Gauge Attachments

B40.200-//2008//	Thermometers, Direct Reading and Remote Reading

F.	American Society for Testing and Materials (ASTM)

A126-//2014//	Standard Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings

B32-08Standard Specification for Solder Metal

B88-//2016//	Standard Specification for Seamless Copper Water Tube

B88M-//2018//	Standard Specification for Seamless Copper Water Tube (Metric)

B280-//2019//	Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service

G.	American Welding Society, Inc. (AWS):Brazing Handbook

A5.8/A5.8M-//2011//	Standard Specification for Filler Metals for Brazing and Braze Welding

H.	Underwriters Laboratories (U.L.):

U.L.207-//2018//	Standard for Refrigerant-Containing Components and Accessories, Nonelectrical

U.L.429-//2013//	Standard for Electrically Operated Valves

PART 2 - PRODUCTS

2.1 piping AND FITTINGS

A.	Refrigerant Piping: For piping up to 100 mm (4 inch) use Copper refrigerant tube, ASTM B280, cleaned, dehydrated and sealed, marked ACR on hard temper straight lengths. Coils shall be tagged ASTM B280 by the manufacturer.  For piping over 100 mm (4 inch) use A53 Black SML steel.

B.	Water and Drain Piping: Copper water tube, ASTM B88M, Type B or C (ASTM B88, Type M or L). Optional drain piping material: Schedule 80 flame retardant Polypropylene plastic.

C.	Fittings, Valves and Accessories:

1.	Copper fittings: Wrought copper fittings, ASME B16.22.

a.	Brazed Joints, refrigerant tubing: Cadmium free, AWS A5.8/A5.8M, 45 percent silver brazing alloy, Class BAg-5.

b.	Solder Joints, water and drain: 95-5 tin-antimony, ASTM B32 (95TA).

2.	Steel fittings: ASTM wrought steel fittings.

a.	Refrigerant piping – Welded Joints.

3.	Flanges and flanged fittings: ASME B16.24.

4.	Refrigeration Valves:

a.	Stop Valves: Brass or bronze alloy, packless, or packed type with gas tight cap, frost proof, back seating.

b.	Pressure Relief Valves: Comply with ASME Boiler and Pressure Vessel Code; UL listed.  Forged brass with nonferrous, corrosion resistant internal working parts of high strength, cast iron bodies conforming to ASTM A126, Grade B. Set valves in accordance with ASHRAE Standard 15.

c.	Solenoid Valves: Comply with ARI 760 and UL 429, UL-listed, two-position, direct acting or pilot-operated, moisture and vapor-proof type of corrosion resisting materials, designed for intended service, and solder-end connections. Fitted with suitable NEMA 250 enclosure of type required by location and normally // open // closed // holding coil.

d.	Thermostatic Expansion Valves: Comply with ARI 750.  Brass body with stainless-steel or non-corrosive nonferrous internal parts, diaphragm and spring-loaded (direct-operated) type with sensing bulb and distributor having side connection for hot-gas bypass and external equalizer. Size and operating characteristics as recommended by manufacturer of evaporator and factory set for superheat requirements. Solder-end connections. Testing and rating in accordance with ASHRAE Standard 17.

e.	Check Valves: Brass or bronze alloy with swing or lift type, with tight closing resilient seals for silent operation; designed for low pressure drop, and with solder-end connections. Direction of flow shall be legibly and permanently indicated on the valve body.

5.	Strainers: Designed to permit removing screen without removing strainer from piping system, and provided with screens 80 to 100 mesh in liquid lines DN 25 (NPS 1) and smaller, 60 mesh in liquid lines larger than DN 25 (NPS 1), and 40 mesh in suction lines. Provide strainers in liquid line serving each thermostatic expansion valve, and in suction line serving each refrigerant compressor not equipped with integral strainer.

6.	Refrigerant Moisture/Liquid Indicators: Double-ported type having heavy sight glasses sealed into forged bronze body and incorporating means of indicating refrigerant charge and moisture indication. Provide screwed brass seal caps.

7.	Refrigerant Filter-Dryers: UL listed, angle or in-line type, as shown on drawings. Conform to ARI Standard 730 and ASHRAE Standard 63.1. Heavy gage steel shell protected with corrosion-resistant paint; perforated baffle plates to prevent desiccant bypass. Size as recommended by manufacturer for service and capacity of system with connection not less than the line size in which installed. Filter driers with replaceable filters shall be furnished with one spare element of each type and size.

8.	Flexible Metal Hose: Seamless bronze corrugated hose, covered with bronze wire braid, with standard copper tube ends. Provide in suction and discharge piping of each compressor.

2.2 GAGES

A.	Temperature Gages: Comply with ASME B40.200. Industrial-duty type and in required temperature range for service in which installed. Gages shall have Celsius scale in 1-degree (Fahrenheit scale in 2-degree) graduations and with black number on a white face. The pointer shall be adjustable. Rigid stem type temperature gages shall be provided in thermal wells located within 1525 mm (5 feet) of the finished floor. Universal adjustable angle type or remote element type temperature gages shall be provided in thermal wells located 1525 to 2135 mm (5 to 7 feet) above the finished floor. Remote element type temperature gages shall be provided in thermal wells located 2135 mm (7 feet) above the finished floor.

B.	Vacuum and Pressure Gages: Comply with ASME B40.100 and provide with throttling type needle valve or a pulsation dampener and shut-off valve. Gage shall be a minimum of 90 mm (3-1/2 inches) in diameter with a range from 0 kPa (0 psig) to approximately 1.5 times the maximum system working pressure. Each gage range shall be selected so that at normal operating pressure, the needle is within the middle-third of the range.

1.	Suction: 101 kPa (30 inches Hg) vacuum to 1723 kPa (gage) (250 psig).

2.	Discharge: 0 to 3445 kPa (gage) (0 to 500 psig).

2.3 PIPE SUPPORTS

A.	Refer to specification Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

2.4 REFRIGERANTs AND OIL

A.	Provide EPA approved refrigerant and oil for proper system operation.

2.5 PIPE INSULATION FOR DX HVAC SYSTEMS

Refer to specification Section 23 07 11, HVAC, PLUMBING, and BOILER PLANT INSULATION.

PART 3 - EXECUTION

3.1 INSTALLATION

A.	Install refrigerant piping and refrigerant containing parts in accordance with ASHRAE Standard 15 and ASME B31.5

1.	Install piping as short as possible, with a minimum number of joints, elbow and fittings.

2.	Install piping with adequate clearance between pipe and adjacent walls and hangers to allow for service and inspection. Space piping, including insulation, to provide 25 mm (1 inch) minimum clearance between adjacent piping or other surface. Use pipe sleeves through walls, floors, and ceilings, sized to permit installation of pipes with full thickness insulation.

3.	Locate and orient valves to permit proper operation and access for maintenance of packing, seat and disc. Generally locate valve stems in overhead piping in horizontal position. Provide a union adjacent to one end of all threaded end valves. Control valves usually require reducers to connect to pipe sizes shown on the drawing.

4.	Use copper tubing in protective conduit when installed below ground.

5.	Install hangers and supports per ASME B31.5 and the refrigerant piping manufacturer's recommendations.

B.	Joint Construction:

1.	Brazed Joints: Comply with AWS "Brazing Handbook" and with filler materials complying with AWS A5.8/A5.8M.

a.	Use Type BcuP, copper-phosphorus alloy for joining copper socket fittings with copper tubing.

b.	Use Type BAg, cadmium-free silver alloy for joining copper with bronze or steel.

c.	Swab fittings and valves with manufacturer's recommended cleaning fluid to remove oil and other compounds prior to installation.

d.	Pass nitrogen gas through the pipe or tubing to prevent oxidation as each joint is brazed. Cap the system with a reusable plug after each brazing operation to retain the nitrogen and prevent entrance of air and moisture.

C.	Protect refrigerant system during construction against entrance of foreign matter, dirt and moisture; have open ends of piping and connections to compressors, condensers, evaporators and other equipment tightly capped until assembly.

D.	Pipe relief valve discharge to outdoors for systems containing more than 45 kg (100 lbs) of refrigerant.

E.	Firestopping: Fill openings around uninsulated piping penetrating floors or fire walls, with firestop material. For firestopping insulated piping refer to Section 23 07 11, HVAC, and BOILER PLANT INSULATION.

F.	Seismic Bracing: Refer to specification Section 13 05 41, SEISMIC RESTRAINTS REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS, for bracing of piping in seismic areas.

3.2 PIPE AND TUBING INSULATION

A.	Refer to specification Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

B.	Apply two coats of weather-resistant finish as recommended by the manufacturer to insulation exposed to outdoor weather.

3.3 Signs and identification

A.	Each refrigerating system erected on the premises shall be provided with an easily legible permanent sign securely attached and easily accessible, indicating thereon the name and address of the installer, the kind and total number of pounds of refrigerant required in the system for normal operations, and the field test pressure applied.

B.	Systems containing more than 50 kg (110 lb) of refrigerant shall be provided with durable signs, in accordance with ANSI A13.1 and ANSI Z535.1, having letters not less than 13 mm (1/2 inch) in height designating:

1.	Valves and switches for controlling refrigerant flow, the ventilation and the refrigerant compressor(s).

2.	Signs on all exposed high pressure and low pressure piping installed outside the machinery room, with name of the refrigerant and the letters "HP" or "LP."

3.4 Field quality control

A.	Prior to initial operation examine and inspect piping system for conformance to plans and specifications and ASME B31.5. Correct equipment, material, or work rejected because of defects or nonconformance with plans and specifications, and ANSI codes for pressure piping.

B.	After completion of piping installation and prior to initial operation, conduct test on piping system according to ASME B31.5. Furnish materials and equipment required for tests. Perform tests in the presence of Resident Engineer. If the test fails, correct defects and perform the test again until it is satisfactorily done and all joints are proved tight.

1.	Every refrigerant-containing parts of the system that is erected on the premises, except compressors, condensers, evaporators, safety devices, pressure gages, control mechanisms and systems that are factory tested, shall be tested and proved tight after complete installation, and before operation.

2.	The high and low side of each system shall be tested and proved tight at not less than the lower of the design pressure or the setting of the pressure-relief device protecting the high or low side of the system, respectively, except systems erected on the premises using non-toxic and non-flammable Group A1 refrigerants with copper tubing not exceeding DN 18 (NPS 5/8). This may be tested by means of the refrigerant charged into the system at the saturated vapor pressure of the refrigerant at 20 degrees C (68 degrees F) minimum.

C.	Test Medium: A suitable dry gas such as nitrogen or shall be used for pressure testing. The means used to build up test pressure shall have either a pressure-limiting device or pressure-reducing device with a pressure-relief device and a gage on the outlet side. The pressure relief device shall be set above the test pressure but low enough to prevent permanent deformation of the system components.

3.5 system test and charging

A.	System Test and Charging: As recommended by the equipment manufacturer or as follows:

1.	Connect a drum of refrigerant to charging connection and introduce enough refrigerant into system to raise the pressure to 70 kPa (10 psi) gage. Close valves and disconnect refrigerant drum. Test system for leaks with halide test torch or other approved method suitable for the test gas used. Repair all leaking joints and retest.

2.	Connect a drum of dry nitrogen to charging valve and bring test pressure to design pressure for low side and for high side. Test entire system again for leaks.

3.	Evacuate the entire refrigerant system by the triplicate evacuation method with a vacuum pump equipped with an electronic gage reading in mPa (microns).  Pull the system down to 665 mPa (500 microns) 665 mPa (2245.6 inches of mercury at 60 degrees F) and hold for four hours then break the vacuum with dry nitrogen (or refrigerant). Repeat the evacuation two more times breaking the third vacuum with the refrigeration to be charged and charge with the proper volume of refrigerant.

- - - E N D - - -