SECTION 26 05 19

LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

PART 1 - GENERAL

1.1 DESCRIPTION

A.	This section specifies the furnishing, installation, connection, and testing of the electrical conductors and cables for use in electrical systems rated 600 V and below, indicated as cable(s), conductor(s), wire, or wiring in this section.

1.2 RELATED WORK

A.	Section 07 84 00, FIRESTOPPING: Sealing around penetrations to maintain the integrity of fire-resistant rated construction.

B.	Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS: Requirements that apply to all sections of Division 26.

C.	Section 26 05 26, GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS: Requirements for personnel safety and to provide a low impedance path for possible ground fault currents.

D.	Section 26 05 33, RACEWAY AND BOXES FOR ELECTRICAL SYSTEMS: Conduits for conductors and cables.

1.3 qualITY ASSURANCE

A.	Quality Assurance shall be in accordance with Paragraph, QUALIFICATIONS (PRODUCTS AND SERVICES) in Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS.

1.4 SUBMITTALS

A.	In accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, furnish the following:

1.	Manufacturer's Literature and Data: Showing each cable type and rating.

2.	Certificates: Two weeks prior to final inspection, deliver to the Resident Engineer four copies of the certification that the material is in accordance with the drawings and specifications and has been properly installed.

B.	Submit in accordance with Paragraph, SUBMITTALS in Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS, and the following requirements:

1.	Shop Drawings:

a.	Submit sufficient information to demonstrate compliance with drawings and specifications.

b.	Submit the following data for approval:

1)	Electrical ratings and insulation type for each conductor and cable.

2)	Splicing materials and pulling lubricant.

2.	Certifications: Two weeks prior to final inspection, submit the following.

a.	Certification by the manufacturer that the conductors and cables conform to the requirements of the drawings and specifications.

b.	Certification by the Contractor that the conductors and cables have been properly installed, adjusted, and tested.

1.5 APPLICABLE PUBLICATIONS

A.	Publications listed below (including amendments, addenda, revisions, supplements and errata) form a part of this specification to the extent referenced. Publications are reference in the text by designation only.

B.	American Society of Testing Material (ASTM):

D2301-10	Standard Specification for Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape

D2304-10	Test Method for Thermal Endurance of Rigid Electrical Insulating Materials

D3005-10	Low-Temperature Resistant Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape

C.	National Electrical Manufacturers Association (NEMA):

WC 70-09	Power Cables Rated 2000 Volts or Less for the Distribution of Electrical Energy

D.	National Fire Protection Association (NFPA):

70-17	National Electrical Code (NEC)

E.	Underwriters Laboratories, Inc. (UL):

44-14	Thermoset-Insulated Wires and Cables

83-14	Thermoplastic-Insulated Wires and Cables

467-13	Grounding and Bonding Equipment

486A-486B-13	Wire Connectors

486C-13	Splicing Wire Connectors

486D-15	Sealed Wire Connector Systems

486E-15	Equipment Wiring Terminals for Use with Aluminum and/or Copper Conductors

493-07	Thermoplastic-Insulated Underground Feeder and Branch Circuit Cables

514B-12	Conduit, Tubing, and Cable Fittings

PART 2 - PRODUCTS

2.1 conductors and CABLES

A.	Conductors and cables shall be in accordance with ASTM, NEMA, NFPA, UL, as specified herein, and as shown on the drawings.

B.	All conductors shall be copper.

C.	Single Conductor and Cable:

1.	No. 12 AWG: Minimum size, except where smaller sizes are specified herein or shown on the drawings.

2.	No. 8 AWG and larger: Stranded.

3.	No. 10 AWG and smaller: Solid; except shall be stranded for final connection to motors, transformers, and vibrating equipment.

4.	Insulation: THHN-THWN and XHHW.

D.	Color Code:

1.	No. 10 AWG and smaller: Solid color insulation or solid color coating.

2.	No. 8 AWG and larger: Color-coded using one of the following methods:

a.	Solid color insulation or solid color coating.

b.	Stripes, bands, or hash marks of color specified.

c.	Color using 19 mm (0.75 inches) wide tape.

4.	For modifications and additions to existing wiring systems, color coding shall conform to the existing wiring system.

5.	Conductors shall be color-coded as follows:

| 208/120 V | Phase | 480/277 V |
| --- | --- | --- |
| Black | A | Brown |
| Red | B | Orange |
| Blue | C | Yellow |
| White | Neutral | Gray * |
| * or white with colored (other than green) tracer. |  |  |

6.	Lighting circuit “switch legs”, and 3-way and 4-way switch “traveling wires,” shall have color coding that is unique and distinct (e.g., pink and purple) from the color coding indicated above. The unique color codes shall be solid and in accordance with the NEC. Coordinate color coding in the field with the COR.

2.2 SPLICES

A.	Splices shall be in accordance with NEC and UL.

B.	Above Ground Splices for No. 10 AWG and Smaller:

1.	Solderless, screw-on, reusable pressure cable type, with integral insulation, approved for copper and aluminum conductors.

2.	The integral insulator shall have a skirt to completely cover the stripped conductors.

3.	The number, size, and combination of conductors used with the connector, as listed on the manufacturer's packaging, shall be strictly followed.

2.3 CONTROL WIRING

A.	Unless otherwise specified elsewhere in these specifications, control wiring shall be as specified herein, except that the minimum size shall be not less than No. 14 AWG.

B.	Control wiring shall be sized such that the voltage drop under in-rush conditions does not adversely affect operation of the controls.

2.4 WIRE LUBRICATING COMPOUND

A.	Lubricating compound shall be suitable for the wire insulation and conduit, and shall not harden or become adhesive.

PART 3 - EXECUTION

3.1 GENERAl

A.	Installation shall be in accordance with the NEC, as shown on the drawings, and manufacturer’s instructions.

B.	Install all conductors in raceway systems.

C.	Splice conductors only in outlet boxes, junction boxes, pullboxes, manholes, or handholes.

D.	Conductors of different systems (e.g., 120 V and 277 V) shall not be installed in the same raceway.

E.	Install cable supports for all vertical feeders in accordance with the NEC. Provide split wedge type which firmly clamps each individual cable and tightens due to cable weight.

F.	In panelboards, cabinets, wireways, switches, enclosures, and equipment assemblies, neatly form, train, and tie the conductors with non-metallic ties.

G.	Conductor and Cable Pulling:

1.	Provide installation equipment that will prevent the cutting or abrasion of insulation during pulling. Use lubricants approved for the cable.

2.	Use nonmetallic pull ropes.

3.	Attach pull ropes by means of either woven basket grips or pulling eyes attached directly to the conductors.

4.	All conductors in a single conduit shall be pulled simultaneously.

H.	No more than three branch circuits shall be installed in any one conduit.

I.	When stripping stranded conductors, use a tool that does not damage the conductor or remove conductor strands.

3.2 SPLICE and termination INSTALLATION

A.	Splices and terminations shall be mechanically and electrically secure, and tightened to manufacturer’s published torque values using a torque screwdriver or wrench.

B.	Where the Government determines that unsatisfactory splices or terminations have been installed, replace the splices or terminations at no additional cost to the Government.

3.3 conductor identification

A.	When using colored tape to identify phase, neutral, and ground conductors larger than No. 8 AWG, apply tape in half-overlapping turns for a minimum of 75 mm (3 inches) from terminal points, and in junction boxes, pullboxes, and manholes. Apply the last two laps of tape with no tension to prevent possible unwinding. Where cable markings are covered by tape, apply tags to cable, stating size and insulation type.

3.4 FEEDER conductor IDENTIFICATION

A.	In each interior pullbox and each underground manhole and handhole, install brass tags on all feeder conductors to clearly designate their circuit identification and voltage. The tags shall be the embossed type, 40 mm (1-1/2 inches) in diameter and 40 mils thick. Attach tags with plastic ties.

3.5 existIng conductors

A.	Unless specifically indicated on the plans, existing conductors shall not be reused.

3.6 CONTROL WIRING INSTALLATION

A.	Unless otherwise specified in other sections, install control wiring and connect to equipment to perform the required functions as specified or as shown on the drawings.

B.	Install a separate power supply circuit for each system, except where otherwise shown on the drawings.

3.7 CONTROL wiring IDENTIFICATION

A.	Install a permanent wire marker on each wire at each termination.

B.	Identifying numbers and letters on the wire markers shall correspond to those on the wiring diagrams used for installing the systems.

C.	Wire markers shall retain their markings after cleaning.

3.8 Acceptance Checks and Tests

A.	Perform in accordance with the manufacturer's recommendations.  In addition, include the following:

1.	Visual Inspection and Tests: Inspect physical condition.

2.	Electrical tests:

a.	After installation but before connection to utilization devices, such as fixtures, motors, or appliances, test conductors phase-to-phase and phase-to-ground resistance with an insulation resistance tester.  Existing conductors to be reused shall also be tested.

b.	Applied voltage shall be 500 V DC for 300 V rated cable, and 1000 V DC for 600 V rated cable. Apply test for one minute or until reading is constant for 15 seconds, whichever is longer. Minimum insulation resistance values shall not be less than 25 megohms for 300 V rated cable and 100 megohms for 600 V rated cable.

c.	Perform phase rotation test on all three-phase circuits.

---END---