SECTION 26 27 26
WIRING DEVICES

PART 1 - GENERAL

1.1 DESCRIPTION

A.	This section specifies the furnishing, installation, connection, and testing of wiring devices.

1.2 RELATED WORK

A.	Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS: General electrical requirements that are common to more than one section of Division 26.

B.	Section 26 05 19, LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES: Cables and wiring.

C.	Section 26 05 26, GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS: Requirements for personnel safety and to provide a low impedance path to ground for possible ground fault currents.

D.	Section 26 05 33, RACEWAY AND BOXES FOR ELECTRICAL SYSTEMS: Conduit and boxes.

1.3 qualITY ASSURANCE

A.	Refer to Paragraph, QUALIFICATIONS (PRODUCTS AND SERVICES), in Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS.

1.4 SUBMITTALS

A.	Submit six copies of the following in accordance with Section 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS.

1.	Shop Drawings:

a.	Submit sufficient information to demonstrate compliance with drawings and specifications.

b.	Include electrical ratings, dimensions, mounting details, construction materials, grade, and termination information.

2.	Manuals:

a.	Submit, simultaneously with the shop drawings, companion copies of complete maintenance and operating manuals, including technical data sheets and information for ordering replacement parts.

b.	If changes have been made to the maintenance and operating manuals originally submitted, submit updated maintenance and operating manuals two weeks prior to the final inspection.

3.	Certifications: Two weeks prior to final inspection, submit the following.

a.	Certification by the manufacturer that the wiring devices conform to the requirements of the drawings and specifications.

b.	Certification by the Contractor that the wiring devices have been properly installed and adjusted.

1.5 APPLICABLE PUBLICATIONS

A.	Publications listed below (including amendments, addenda, revisions, supplements and errata) form a part of this specification to the extent referenced. Publications are referenced in the text by basic designation only.

B.	National Fire Protection Association (NFPA):

70-14	National Electrical Code (NEC)

99-15	Health Care Facilities

C.	National Electrical Manufacturers Association (NEMA):

WD 1-10	General Color Requirements for Wiring Devices

WD 6-12 	Wiring Devices – Dimensional Specifications

D.	Underwriter’s Laboratories, Inc. (UL):

5-11	Surface Metal Raceways and Fittings

20-10	General-Use Snap Switches

231-08	Power Outlets

467-13	Grounding and Bonding Equipment

498-12	Attachment Plugs and Receptacles

943-15	Ground-Fault Circuit-Interrupters

1449-14	Surge Protective Devices

1472-15	Solid State Dimming Controls

pART 2 - PRODUCTS

2.1 RECEPTACLES

A.	General: All receptacles shall comply with NEMA, NFPA, UL, and as shown on the drawings.

1.	Mounting straps shall be nickel plated brass, brass, nickel plated steel or galvanize steel with break-off plaster ears, and shall include a self-grounding feature.  Terminal screws shall be brass, brass plated or a copper alloy metal.

2.	Receptacles shall have provisions for back wiring with separate metal clamp type terminals (four minimum) and side wiring from four captively held binding screws.

B.	Duplex Receptacles - Hospital-grade: shall be listed for hospital grade, single phase, 20 ampere, 120 volts, 2-pole, 3-wire, NEMA 5-20R, with break-off feature for two-circuit operation.

1.	Bodies shall be ivory in color.

2.	Switched duplex receptacles shall be wired so that only the top receptacle is switched. The lower receptacle shall be unswitched.

3.	Duplex Receptacles on Emergency Circuit:

a.	In rooms without emergency powered general lighting, the emergency receptacles shall be of the self-illuminated type.

4.	Ground Fault Current Interrupter (GFCI) Duplex Receptacles: Shall be an integral unit, hospital-grade, suitable for mounting in a standard outlet box, with end-of-life indication and provisions to isolate the face due to improper wiring. GFCI receptacles shall be self-test receptacles in accordance with UL 943.

a.	Ground fault interrupter shall consist of a differential current transformer, self-test, solid state sensing circuitry and a circuit interrupter switch. Device shall have nominal sensitivity to ground leakage current of 4-6 milliamperes and shall function to interrupt the current supply for any value of ground leakage current above five milliamperes (+ or – 1 milliampere) on the load side of the device. Device shall have a minimum nominal tripping time of 0.025 second.

b.	Self-test function shall be automatically initiated within 5 seconds after power is activated to the receptacles. Self-test function shall be periodically and automatically performed every 3 hours or less.

c.	End-of-life indicator light shall be a persistent flashing or blinking light to indicate that the GFCI receptacle is no longer in service.

5.	Tamper-Resistant Duplex Receptacles:

a.	Bodies shall be gray in color.

1)	Shall permit current to flow only while a standard plug is in the proper position in the receptacle.

2)	Screws exposed while the wall plates are in place shall be the tamperproof type.

C.	Duplex Receptacles – Non-hospital Grade:  shall be the same as duplex receptacles – hospital grade in accordance with sections 2.1A and 2.1B of this specification, except for the hospital grade listing.

a.	Bodies shall be brown nylon.

D.	Receptacles - 20, 30, and 50 ampere, 250 Volts: Shall be complete with appropriate cord grip plug.

E.	Weatherproof Receptacles: Shall consist of a duplex receptacle, mounted in box with a gasketed, weatherproof, cast metal cover plate and cap over each receptacle opening. The cap shall be permanently attached to the cover plate by a spring-hinged flap. The weatherproof integrity shall not be affected when heavy duty specification or hospital grade attachment plug caps are inserted. Cover plates on outlet boxes mounted flush in the wall shall be gasketed to the wall in a watertight manner.

PART 3 - EXECUTION

3.1 INSTALLATION

A.	Installation shall be in accordance with the NEC and as shown as on the drawings.

B.	The ground terminal of each wiring device shall be bonded to the outlet box with an approved green bonding jumper, and also connected to the branch circuit equipment grounding conductor.

C.	Exact field locations of floors, walls, partitions, doors, windows, and equipment may vary from locations shown on the drawings. Prior to locating sleeves, boxes and chases for roughing-in of conduit and equipment, the Contractor shall coordinate exact field location of the above items with other trades.

D.	Install receptacles at heights approved by VA Resident Engineer or COR.

E.	When required or recommended by the manufacturer, use a torque screwdriver.  Tighten unused terminal screws.

F.	Label device plates with a permanent adhesive label listing panel and circuit feeding the wiring device.

3.2 Acceptance Checks and Tests

A.	Perform manufacturer’s required field checks in accordance with the manufacturer's recommendations, and the latest NFPA 99. In addition, include the following:

1.	Visual Inspection and Tests:

a.	Inspect physical and electrical conditions.

b.	Vacuum-clean surface metal raceway interior.  Clean metal raceway exterior.

c.	Test wiring devices for damaged conductors, high circuit resistance, poor connections, inadequate fault current path, defective devices, or similar problems using a portable receptacle tester.  Correct circuit conditions, remove malfunctioning units and replace with new, and retest as specified above.

d.	Test GFCI receptacles.

---END---