**ADDENDUM No. 3**

Date: 5/26/2022

**DORMITORY AUTHORITY - STATE OF NEW YORK**

**Rockland Psychiatric Center
Cook Chill Production Center**

**BMS Replacement**

**Project # 3608809999**

This **ADDENDUM** is hereby included in and made part of the Contract whether or not attached thereto. All requirements of the original Specifications and Drawings shall remain in force except as noted by this **ADDENDUM No.** **3**

**THE PURPOSE OF THIS ADDENDUM IS TO CHANGE THE FOLLOWING ITEMS:**

**The following revisions and additions shall become part of the bid documents. This Addendum permits abandonment of concealed pneumatic tubing:**

|  |
| --- |
| The existing controls are primarily pneumatic, being served by pneumatic tubing. The documents require abandoned tubing to be remove and all structure (walls/floors) to be patched.This addendum permits pneumatic tubbing that is concealed (inside walls and above suspended ceilings) to be abandoned in place. All tubing to remain is to be capped where being disconnected. Abandoned tubing is to be labeled “Not In Use” every 25 feet and at all points of disconnection. All exposed tubing is to be removed. All exposed walls/floors/ceilings are to be patched, painted, and sealed per specification 017329 and 099123, where tubing is removed/penetrates the structure.The pneumatic line removal notes on sheets DM-101, DM-102, DM-103, DM-104 and DM-105 remain as written. Where exposed sensors are removed, the tubing is to be cut back, capped and wall patches and painted as necessary, per notes on DM drawings. |
|  |
|  |
|  |
|  |
| **END OF ADDENDUM NO. 3** |