April 13, 2022

Coppola

28 Executive Parkway

Ringwood, NJ 07456

**RE:** **Suez PFAS D Compliance Project –HVAC**

**RFI#1**

* Is the duct work that is to be installed galvanized or Stainless Steel?
  + **SCE Comment**: No preference for material.
* The drawings do not show any grilles in the ductwork. Are grilles to be provided & installed or Expanded Metal at the end of the duct run?
  + **SCE Comment**: Grilles are to be provided.
* The louver detail calls for a manually operated louver.
  + **SCE Comment**: Acknowledged, Manual louvers are acceptable.
* Is the louver to have a volume control damper or a backdraft damper?
  + SCE Comment: Backdraft dampers are acceptable
* **SCE General Note**:
  + Air conditioning is not to be provided, exhaust fan operated by a thermostat and inline duct heaters are to be installed at the facilities.

Thank you

Karen Panarella