SECTION 232213

STEAM AND CONDENSATE HEATING PIPING

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

*Use this Specification Section for Mail Processing Facilities.*

***This is a Type 2 Specification with primarily editable text; therefore, most of the text can be edited, but there is some required text which is noted within the Section with a “Note to Specifier.” Do not revise these paragraphs without an approved Deviation from USPS Headquarters, Facilities Program Management, through the USPS Project Manager.***

*For Design/Build projects, do not delete the Notes to Specifier in this Section so that they may be available to Design/Build entity when preparing the Construction Documents.*

*For the Design/Build entity, this specification is intended as a guide for the Architect/Engineer preparing the Construction Documents.*

*The MPF specifications may also be used for Design/Bid/Build projects. In either case, it is the responsibility of the design professional to edit the Specifications Sections as appropriate for the project.*

*Text shown in brackets must be modified as needed for project specific requirements.* *See the “Using the USPS Guide Specifications” document in Folder C for more information.*

*The last date that USPS revised this standard specification section occurs in two places, at the end of this section and in the Table of Contents. If the date in this section matches the date in the Table of Contents, then you are using the latest version. Do not delete or revise the “last revised” date at the end of the section during the development of the Project Manual.*

*The footer in this section should be edited to replace the text, “USPS MPF SPECIFICATION” with the project name, and the blank date in the center should be replaced with the submission date, for interim design reviews, or the issue date of the completed Project Manual.*

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

1. GENERAL
   1. SUMMARY
      1. This Section includes the following for LP steam (less than 30 psig) and condensate piping:
         1. Pipe and fittings.
         2. Strainers.
         3. Safety valves.
         4. Pressure-reducing valves.
         5. Steam traps.
         6. Thermostatic air vents and vacuum breakers.
   2. PERFORMANCE REQUIREMENTS
      1. Components and installation shall be capable of withstanding the following minimum working pressures and temperatures:
         1. LP Steam Piping:
         2. Condensate Piping: 100 psig at 250 deg F.
         3. Makeup-Water Piping: 100 psig at 150 deg F.
         4. Blowdown-Drain Piping: Equal to pressure of the piping system to which it is attached.
         5. Air-Vent and Vacuum-Breaker Piping: Equal to pressure of the piping system to which it is attached.
         6. Safety-Valve-Inlet and -Outlet Piping: Equal to pressure of the piping system to which it is attached.
   3. SUBMITTALS
      1. Product Data: For each type of the following:
         1. Pressure-reducing and safety valve.
         2. Steam trap.
         3. Air vent and vacuum breaker.
      2. Shop Drawings: Detail, 1/4 inch equals 1 foot scale, fabrication of pipe anchors, hangers, pipe, multiple pipes, alignment guides, and expansion joints and loops and their attachment to the building structure. Detail locations of anchors, alignment guides, and expansion joints and loops.
      3. Field quality-control test reports.
      4. Operation and maintenance data.
   4. QUALITY ASSURANCE
      1. ASME Compliance: Comply with ASME B31.9, "Building Services Piping" for materials, products, and installation. Safety valves and pressure vessels shall bear the appropriate ASME label.
2. PRODUCTS

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

*\*\*Required: Piping and fittings materials must comply with the chart in Section 220000 - Plumbing*

*Do not revise the materials below without an approved deviation; however, items may be removed to comply with local code requirements or for building requirements for MPF Repair & Alteration or Expansion projects; verify with the facility.*

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* 1. COPPER TUBE AND FITTINGS
     1. Drawn-Temper Copper Tubing: ASTM B 88, Type L.
     2. Annealed-Temper Copper Tubing: ASTM B 88, Type K.
     3. Wrought-Copper Fittings and Unions: ASME B16.22.
  2. STEEL PIPE AND FITTINGS
     1. Steel Pipe: ASTM A 53/A 53M, black steel, plain ends, Type, Grade, and Schedule as indicated in Part 3 piping applications articles.
     2. Cast-Iron Threaded Fittings: ASME B16.4; Classes 125, 150, and 300 as indicated in Part 3 piping applications articles.
     3. Malleable-Iron Threaded Fittings: ASME B16.3; Classes 150 and 300 as indicated in Part 3 piping applications articles.
     4. Malleable-Iron Unions: ASME B16.39; Classes 150, 250, and 300 as indicated in Part 3 piping applications articles.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Coordinate flange class in first paragraph below with products in other parts of this Section and in related. Sections to match face size and bolt patterns.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Cast-Iron Threaded Flanges and Flanged Fittings: ASME B16.1, Classes 125 and 250 as indicated in Part 3 piping applications articles; raised ground face, and bolt holes spot faced.
    2. Stainless-Steel Bellows, Flexible Connectors:
       1. Body: Stainless-steel bellows with woven, flexible, bronze, wire-reinforced, protective jacket.
       2. End Connections: Threaded or flanged to match equipment connected.
       3. Performance: Capable of 3/4-inch misalignment.
       4. CWP Rating: 150 psig.
       5. Maximum Operating Temperature: 250 deg F.
  1. JOINING MATERIALS
     1. Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.
        1. ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch maximum thickness unless thickness or specific material is indicated.
           1. Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.
           2. Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.
     2. Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.
     3. Solder Filler Metals: ASTM B 32, lead-free alloys. Include water-flushable flux according to ASTM B 813.
     4. Brazing Filler Metals: AWS A5.8, BCuP Series, copper-phosphorus alloys for joining copper with copper; or BAg-1, silver alloy for joining copper with bronze or steel.
  2. DIELECTRIC FITTINGS
     1. Description: Combination fitting of copper alloy and ferrous materials with threaded, solder-joint, plain, or weld-neck end connections that match piping system materials.
     2. Insulating Material: Suitable for system fluid, pressure, and temperature.
     3. Dielectric Unions:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Capitol Manufacturing Company.
           2. Central Plastics Company.
           3. Hart Industries, International Inc.
           4. Watts Water Technologies, Inc.
           5. Zurn Plumbing Products Group.
        2. Factory-fabricated union assembly, for 250-psig minimum working pressure at 180 deg F.
  3. VALVES
     1. Gate, Globe, Check, Ball, and Butterfly Valves: Comply with requirements specified in Division 23 Section "General-Duty Valves for HVAC Piping."
     2. Stop-Check Valves:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Crane Co.
           2. Jenkins Valves; a Crane Company.
           3. Lunkenheimer Valves.
           4. A.Y. McDonald Mfg. Co.
        2. Body and Bonnet: Malleable iron.
        3. End Connections: Flanged.
        4. Disc: Cylindrical with removable liner and machined seat.
        5. Stem: Brass alloy.
        6. Operator: Outside screw and yoke with cast-iron handwheel.
        7. Packing: Polytetrafluoroethylene-impregnated packing with two-piece packing gland assembly.
        8. Pressure Class: 250.
  4. STRAINERS
     1. Y-Pattern Strainers:
        1. Body: ASTM A 126, Class B cast iron, with bolted cover and bottom drain connection.
        2. End Connections: Threaded ends for strainers NPS 2 and smaller; flanged ends for strainers NPS 2-1/2 and larger.
        3. Strainer Screen: Stainless-steel, 20 mesh strainer, and perforated stainless-steel basket with 50 percent free area.
        4. Tapped blowoff plug.
        5. CWP Rating: 250-psig working steam pressure.
  5. SAFETY VALVES

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Valves in paragraph and subparagraphs below are available in NPS 1/2 through NPS 2-1/2 (DN 15 through DN 65).

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Bronze Safety Valves:
       1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
          1. Armstrong International, Inc.
          2. Kunkle Valve; a Tyco International Ltd. Company.
          3. Spirax Sarco, Inc.
          4. Watts Water Technologies, Inc.
       2. Disc Material: Forged copper alloy.
       3. End Connections: Threaded inlet and outlet.
       4. Spring: Fully enclosed steel spring with adjustable pressure range and positive shutoff, factory set and sealed.
       5. Pressure Class: 250.
       6. Drip-Pan Elbow: Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.
       7. Size and Capacity: As required for equipment according to ASME Boiler and Pressure Vessel Code.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Valves in paragraph and subparagraphs below are available in NPS 1-1/2 through NPS 6 (DN 40 through DN 150).

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Cast-Iron Safety Valves:
       1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
          1. Armstrong International, Inc.
          2. Kunkle Valve; a Tyco International Ltd. Company.
          3. Spirax Sarco, Inc.
          4. Watts Water Technologies, Inc.
       2. Disc Material: Forged copper alloy with bronze nozzle.
       3. End Connections: Raised-face flanged inlet and threaded or flanged outlet connections.
       4. Spring: Fully enclosed cadmium-plated steel spring with adjustable pressure range and positive shutoff, factory set and sealed.
       5. Pressure Class: 250.
       6. Drip-Pan Elbow: Cast iron and having threaded inlet, outlet, and drain, with threads complying with ASME B1.20.1.
       7. Exhaust Head: Cast iron and having threaded inlet and drain, with threads complying with ASME B1.20.1.
       8. Size and Capacity: As required for equipment according to ASME Boiler and Pressure Vessel Code.
  1. PRESSURE-REDUCING VALVES
     1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
        1. Armstrong International, Inc.
        2. Hoffman Specialty; Division of ITT Industries.
        3. Leslie Controls, Inc.
        4. Spence Engineering Company, Inc.
        5. Spirax Sarco, Inc.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Schedule pressure-reducing valves and include size, capacity, minimum length of straight pipe on both sides of valve, and inlet and outlet pressures. Select pressure-reducing valves to develop no more than 85 dBA at an elevation of 3 feet above adjacent floor and at 3 feet in any direction. Use Schedule 80 minimum for piping inlet and outlet connections to pressure-reducing valves, to achieve the required sound level, or use sound attenuators.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Size, Capacity, and Pressure Rating: Factory set for inlet and outlet pressures indicated.
    2. Description: Pilot-actuated, diaphragm type, with adjustable pressure range and positive shutoff.
    3. Body: Cast iron.
    4. End Connections: Threaded connections for valves NPS 2 and smaller and flanged connections for valves NPS 2-1/2 and larger.
    5. Trim: Hardened stainless steel.
    6. Head and Seat: Replaceable, main head stem guide fitted with flushing and pressure-arresting device cover over pilot diaphragm.
    7. Gaskets: Non-asbestos materials.
  1. STEAM TRAPS
     1. Thermostatic Traps:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Armstrong International, Inc.
           2. Barnes & Jones, Inc.
           3. Dunham-Bush, Inc.
           4. Hoffman Specialty; Division of ITT Industries.
           5. Spirax Sarco, Inc.
           6. Sterling.
        2. Body: Bronze angle-pattern body with integral union tailpiece and screw-in cap.
        3. Trap Type: Balanced-pressure.
        4. Bellows: Stainless steel or monel.
        5. Head and Seat: Replaceable, hardened stainless steel.
        6. Pressure Class: 125.
     2. Float and Thermostatic Traps:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Armstrong International, Inc.
           2. Barnes & Jones, Inc.
           3. Dunham-Bush, Inc.
           4. Hoffman Specialty; Division of ITT Industries.
           5. Spirax Sarco, Inc.
           6. Sterling.
        2. Body and Bolted Cap: ASTM A 126, cast iron.
        3. End Connections: Threaded.
        4. Float Mechanism: Replaceable, stainless steel.
        5. Head and Seat: Hardened stainless steel.
        6. Trap Type: Balanced pressure.
        7. Thermostatic Bellows: Stainless steel or monel.
        8. Thermostatic air vent capable of withstanding 45 deg F of superheat and resisting water hammer without sustaining damage.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Retain first subparagraph below for optional vacuum breaker.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + - 1. Vacuum Breaker: Thermostatic with phosphor bronze bellows, and stainless steel cage, valve, and seat.
      2. Maximum Operating Pressure: 125 psig.
  1. THERMOSTATIC AIR VENTS AND VACUUM BREAKERS
     1. Thermostatic Air Vents:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Armstrong International, Inc.
           2. Barnes & Jones, Inc.
           3. Dunham-Bush, Inc.
           4. Hoffman Specialty; Division of ITT Industries.
           5. Spirax Sarco, Inc.
           6. Sterling.
        2. Body: Cast iron, bronze, or stainless steel.
        3. End Connections: Threaded.
        4. Float, Valve, and Seat: Stainless steel.
        5. Thermostatic Element: Phosphor bronze bellows in a stainless-steel cage.
        6. Pressure Rating: 125 psig.
        7. Maximum Temperature Rating: 350 deg F.
     2. Vacuum Breakers:
        1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
           1. Armstrong International, Inc.
           2. Dunham-Bush, Inc.
           3. Hoffman Specialty; Division of ITT Industries.
           4. Johnson Corporation (The).
           5. Spirax Sarco, Inc.
        2. Body: Cast iron, bronze, or stainless steel.
        3. End Connections: Threaded.
        4. Sealing Ball, Retainer, Spring, and Screen: Stainless steel.
        5. O-ring Seal: EPR.
        6. Pressure Rating: 125 psig.
        7. Maximum Temperature Rating: 350 deg F.

1. EXECUTION
   1. LP STEAM PIPING APPLICATIONS

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Retain at least one pipe material in paragraphs below for each service required for Project.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. LP Steam Piping: Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.
    2. Condensate Piping above Grade: Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.
    3. Condensate Piping below Grade: Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.
  1. ANCILLARY PIPING APPLICATIONS
     1. Makeup-water piping installed above grade shall be the following:
        1. Drawn-temper copper tubing, wrought-copper fittings, and soldered joints.
     2. Makeup-Water Piping Installed below Grade and within Slabs: Annealed-temper copper tubing, wrought-copper fittings, and soldered joints. Use the fewest possible joints.
     3. Blowdown-Drain Piping: Same materials and joining methods as for piping specified for the service in which blowdown drain is installed.
     4. Air-Vent Piping:
        1. Inlet: Same as service where installed.
        2. Outlet: Type K annealed-temper copper tubing with soldered or flared joints.
     5. Vacuum-Breaker Piping: Outlet, same as service where installed.
     6. Safety-Valve-Inlet and -Outlet Piping: Same materials and joining methods as for piping specified for the service in which safety valve is installed.
  2. VALVE APPLICATIONS
     1. Install shutoff duty valves at branch connections to steam supply mains, at steam supply connections to equipment, and at the outlet of steam traps.
     2. Install safety valves on pressure-reducing stations and elsewhere as required by ASME Boiler and Pressure Vessel Code. Install safety-valve discharge piping, without valves, to nearest floor drain or as indicated on Drawings. Comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1, for installation requirements.
  3. PIPING INSTALLATION
     1. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Use indicated piping locations and arrangements if such were used to size pipe and calculate friction loss, expansion, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.
     2. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.
     3. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.
     4. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.
     5. Install piping to permit valve servicing.
     6. Install piping free of sags and bends.
     7. Install fittings for changes in direction and branch connections.
     8. Install piping to allow application of insulation.
     9. Select system components with pressure rating equal to or greater than system operating pressure.
     10. Install groups of pipes parallel to each other, spaced to permit applying insulation and servicing of valves.
     11. Install drains, consisting of a tee fitting, NPS 3/4 full port-ball valve, and short NPS 3/4 threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.
     12. Install steam supply piping at a minimum uniform grade of 0.2 percent downward in direction of steam flow.
     13. Install condensate return piping at a minimum uniform grade of 0.4 percent downward in direction of condensate flow.
     14. Reduce pipe sizes using eccentric reducer fitting installed with level side down.
     15. Install branch connections to mains using mechanically formed tee fittings in main pipe, with the branch connected to top of main pipe.
     16. Install valves according to Division 23 Section "General-Duty Valves for HVAC Piping."
     17. Install unions in piping, NPS 2 and smaller, adjacent to valves, at final connections of equipment, and elsewhere as indicated.
     18. Install flanges in piping, NPS 2-1/2 and larger, at final connections of equipment and elsewhere as indicated.
     19. Install strainers on supply side of control valves, pressure-reducing valves, traps, and elsewhere as indicated. Install NPS 3/4 nipple and full port ball valve in blowdown connection of strainers NPS 2 and larger. Match size of strainer blowoff connection for strainers smaller than NPS 2.
     20. Install expansion loops, expansion joints, anchors, and pipe alignment guides as specified in Division 23 Section "Expansion Fittings and Loops for HVAC Piping."
     21. Identify piping as specified in Division 23 Section "Identification for HVAC Piping and Equipment."
     22. Install drip legs at low points and natural drainage points such as ends of mains, bottoms of risers, and ahead of pressure regulators, and control valves.
         1. On straight runs with no natural drainage points, install drip legs at intervals not exceeding 300 feet.
         2. Size drip legs same size as main. In steam mains NPS 6 and larger, drip leg size can be reduced, but to no less than NPS 4.
  4. STEAM-TRAP INSTALLATION
     1. Install steam traps in accessible locations as close as possible to connected equipment.
     2. Install full-port ball valve, strainer, and union upstream from trap; install union, check valve, and full-port ball valve downstream from trap unless otherwise indicated.
  5. PRESSURE-REDUCING VALVE INSTALLATION

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Consult manufacturers for proper installation of piping to and from pressure-reducing valves.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Install pressure-reducing valves in accessible location for maintenance and inspection.
    2. Install bypass piping around pressure-reducing valves, with globe valve equal in size to area of pressure-reducing valve seat ring, unless otherwise indicated.
    3. Install gate valves on both sides of pressure-reducing valves.
    4. Install unions or flanges on both sides of pressure-reducing valves having threaded- or flanged-end connections respectively.
    5. Install pressure gages on low-pressure side of pressure-reducing valves after the bypass connection according to Division 23 Section "Meters and Gages for HVAC Piping."
    6. Install strainers upstream for pressure-reducing valve.
    7. Install safety valve downstream from pressure-reducing valve station.
  1. SAFETY VALVE INSTALLATION
     1. Install safety valves according to ASME B31.9, "Building Services Piping."
     2. Pipe safety-valve discharge without valves to atmosphere outside the building.
     3. Install drip-pan elbow fitting adjacent to safety valve and pipe drain connection to nearest floor drain.
     4. Install exhaust head with drain to waste, on vents equal to or larger than NPS 2-1/2.
  2. HANGERS AND SUPPORTS

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Piping support must account for expansion and contraction, vibration, dead load of piping and its contents.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Install hangers and supports according to Division 23 Section "Hangers and Supports for HVAC Piping and Equipment." Comply with requirements below for maximum spacing.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

**NOTE TO SPECIFIER**

Retain first paragraph below for projects in areas that require seismic restraints.

\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*\*

* + 1. Seismic restraints are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."
    2. Install the following pipe attachments:
       1. Adjustable steel clevis hangers for individual horizontal piping less than 20 feet long.
       2. Adjustable roller hangers and spring hangers for individual horizontal piping 20 feet or longer.
       3. Pipe Roller: MSS SP-58, Type 44 for multiple horizontal piping 20 feet or longer, supported on a trapeze.
       4. Spring hangers to support vertical runs.
    3. Install hangers with the following maximum spacing and minimum rod sizes:
       1. NPS 3/4: Maximum span, 9 feet; minimum rod size, 1/4 inch.
       2. NPS 1: Maximum span, 9 feet; minimum rod size, 1/4 inch.
       3. NPS 1-1/2: Maximum span, 12 feet; minimum rod size, 3/8 inch.
       4. NPS 2: Maximum span, 13 feet; minimum rod size, 3/8 inch.
       5. NPS 2-1/2: Maximum span, 14 feet; minimum rod size, 3/8 inch.
       6. NPS 3: Maximum span, 15 feet; minimum rod size, 3/8 inch.
       7. NPS 4: Maximum span, 17 feet; minimum rod size, 1/2 inch.
    4. Install hangers for drawn-temper copper piping with the following maximum spacing and minimum rod sizes:
       1. NPS 1/2: Maximum span, 4 feet; minimum rod size, 1/4 inch.
       2. NPS 3/4: Maximum span, 5 feet; minimum rod size, 1/4 inch.
       3. NPS 1: Maximum span, 6 feet; minimum rod size, 1/4 inch.
       4. NPS 1-1/2: Maximum span, 8 feet; minimum rod size, 3/8 inch.
       5. NPS 2: Maximum span, 8 feet; minimum rod size, 3/8 inch.
       6. NPS 2-1/2: Maximum span, 9 feet; minimum rod size, 3/8 inch.
       7. NPS 3: Maximum span, 10 feet; minimum rod size, 3/8 inch.
    5. Support vertical runs at roof, at each floor, and at 10-foot intervals between floors.
  1. PIPE JOINT CONSTRUCTION
     1. Join pipe and fittings according to the following requirements and Division 23 Sections specifying piping systems.
     2. Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.
     3. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.
     4. Soldered Joints: Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube ends. Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.
     5. Brazed Joints: Construct joints according to AWS's "Brazing Handbook," Chapter "Pipe and Tube," using copper-phosphorus brazing filler metal complying with AWS A5.8.
     6. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:
        1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.
        2. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.
     7. Flanged Joints: Select appropriate gasket material, size, type, and thickness for service application. Install gasket concentrically positioned. Use suitable lubricants on bolt threads.
  2. TERMINAL EQUIPMENT CONNECTIONS
     1. Size for supply and return piping connections shall be the same as or larger than equipment connections.
     2. Install traps and control valves in accessible locations close to connected equipment.
     3. Install bypass piping with globe valve around control valve. If parallel control valves are installed, only one bypass is required.
     4. Install vacuum breakers downstream from control valve, close to coil inlet connection.
     5. Install a drip leg at coil outlet.
  3. FIELD QUALITY CONTROL
     1. Prepare steam and condensate piping according to ASME B31.9, "Building Services Piping," and as follows:
        1. Leave joints, including welds, uninsulated and exposed for examination during test.
        2. Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure. If temporary restraints are impractical, isolate expansion joints from testing.
        3. Flush system with clean water. Clean strainers.
        4. Isolate equipment from piping. If a valve is used to isolate equipment, its closure shall be capable of sealing against test pressure without damage to valve. Install blinds in flanged joints to isolate equipment.
     2. Perform the following tests on steam and condensate piping:
        1. Use ambient temperature water as a testing medium unless there is risk of damage due to freezing. Another liquid that is safe for workers and compatible with piping may be used.
        2. Subject piping system to hydrostatic test pressure that is not less than 1.5 times the working pressure. Test pressure shall not exceed maximum pressure for any vessel, pump, valve, or other component in system under test. Verify that stress due to pressure at bottom of vertical runs does not exceed 90 percent of specified minimum yield strength.
        3. After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage. Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.
     3. Prepare written report of testing.

END OF SECTION

USPS MPF Specification Last Revised: 10/1/2022