SECTION 23 37 00
AIR OUTLETS AND INLETS

# PART 1 - GENERAL

# 1.1 DESCRIPTION

A.	Roof Curbs

B.	Air Outlets and Inlets: Diffusers, Registers, and Grilles.

# 1.2 RELATED WORK

A.	Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES.

B.	NA

C.	Section 13 05 41, SEISMIC RESTRAINT REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS.

D.	Section 23 05 11, COMMON WORK RESULTS FOR HVAC and STEAM GENERATION.

E.	Section 23 05 41, NOISE and VIBRATION CONTROL FOR HVAC PIPING and EQUIPMENT.

F.	Section 23 05 93, TESTING, ADJUSTING, and BALANCING FOR HVAC.

G.	NA

# 1.3 QUALITY ASSURANCE

A.	Refer to Article, QUALITY ASSURANCE, in Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

B.	Fire Safety Code: Comply with NFPA 90A.

# 1.4 SUBMITTALS

A.	Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES.

B.	Manufacturer's Literature and Data:

1.	Air intake/exhaust hoods.

2.	Diffusers, registers, grilles and accessories.

C.	Coordination Drawings: Refer to article, SUBMITTALS, in Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

# 1.5 APPLICABLE PUBLICATIONS

A.	The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B.	Air Diffusion Council Test Code:

1062 GRD-2015	Certification, Rating, and Test Manual 4th Edition

C.	American Society of Civil Engineers (ASCE):

ASCE7-2017	Minimum Design Loads for Buildings and Other Structures

D.	American Society for Testing and Materials (ASTM):

A167-99 2009	Standard Specification for Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet and Strip

B209- 2014	Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

E.	National Fire Protection Association (NFPA):

90A-2018	Standard for the Installation of Air Conditioning and Ventilating Systems

F.	Underwriters Laboratories, Inc. (UL):

181-2013	UL Standard for Safety Factory-Made Air Ducts and Connectors

# PART 2 - PRODUCTS

# 2.1 Gravity INTAKE/EXHAUST Ventilators (ROOF MOUNTED)

A.	Aluminum, ASTM B209, louvered, spun, or fabricated using panel sections with roll-formed edges, 13 mm (1/2 inch) mesh aluminum welded wire bird screen, with gravity or motorized dampers where shown, accessible interior, designed for wind velocity specified in Paragraph 3.3.

1.	Spun Intake/Exhaust Ventilators: Spun aluminum structural components shall be constructed of minimum 1.3 mm (16 Gauge) marine alloy aluminum, bolted to a rigid aluminum support structure.  The aluminum base shall have continuously welded curb cap corners for maximum leak protection.  The spun aluminum baffle shall have a rolled bead for added strength.

2.	Louvered Intake/Exhaust Hoods: Louvered hood constructed from 0.081 Gauge extruded aluminum tiers welded to a minimum 3.3 mm (8 Gauge) aluminum support structure.  The aluminum hood shall be constructed of a minimum 0.064 marine alloy aluminum and provided with a layer of anti-condensate coating.  The aluminum base shall have continuously welded curb cap corners for maximum leak protection.

3.	Low Silhouette Intake/Exhaust Ventilator: The unit shall be of bolted and welded construction utilizing corrosion resistant fasteners. The aluminum hood shall be constructed of minimum 1.60 mm (14 Gauge) marine alloy aluminum, bolted to a minimum 3.25 mm (8 Gauge) aluminum support structure. The aluminum base shall have continuously welded curb cap corners for maximum leak protection. Birdscreen constructed of 13 mm (1/2 inch) mesh shall be mounted across the relief opening.

B.	See ventilator schedule on the drawings. Sizes shown on the drawings designate throat size. Area of ventilator perimeter opening shall be not less than the throat area.

C.	Dampers for Gravity Ventilators without Duct Connection: Construct damper of the same material as the ventilator and of the design to completely close opening or remain wide open. Hold damper in closed position by a brass chain and catch. Extend chains 300 mm (12 inches) below and engage catch when damper is closed.

//D.	See paragraph 3.3 for Intake/Exhaust exposed to high wind

velocities. //

E.	Provide Roof Curb by unit manufacturer.  Refer to Section 23 05 11, COMMON WORK RESULTS FOR HVAC for additional requirements.

# 2.2 EQUIPMENT SUPPORTS

Refer to Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

# 2.3 AIR OUTLETS AND INLETS

A.	Materials:

1.	Steel or aluminum except that all supply air outlets installed in operating rooms and Cystoscopy rooms (see Article 2.3C.3) shall be stainless steel.  Use aluminum air outlets and inlets for facilities located in high-humidity areas.  Exhaust air registers located in combination toilets and shower stalls shall be constructed from aluminum. Provide manufacturer's standard gasket.

2.	Exposed Fastenings: The same material as the respective inlet or outlet. Fasteners for aluminum may be stainless steel.

3.	Contractor shall review all ceiling drawings and details and provide all ceiling mounted devices with appropriate dimensions and trim for the specific locations.

B.	Performance Test Data: In accordance with Air Diffusion Council Code 1062GRD. Refer to Section 23 05 41, NOISE and VIBRATION CONTROL FOR HVAC PIPING and EQUIPMENT for NC criteria.

C.	Air Supply Outlets:

1.	Ceiling Diffusers: Suitable for surface mounting, exposed T-bar or special tile ceilings, off-white finish, square or round neck connection as shown on the drawings. Provide plaster frame for units in plaster ceilings.

a.	Square, louver, fully adjustable pattern: Round neck, surface mounting unless shown otherwise on the drawings. Provide equalizing or control grid and volume control damper.

b.	Louver face type: Square or rectangular, removable core for 1, 2, 3, or 4 way directional pattern. Provide equalizing or control grid and opposed blade damper.

c.	Perforated face type: Manual adjustment for one-, two-, three-, or four-way horizontal air distribution pattern without change of air volume or pressure. Provide equalizing or control grid and opposed blade over overlapping blade damper. Perforated face diffusers for VAV systems shall have the pattern controller on the inner face, rather than in the neck and designed to discharge air horizontally at the ceiling maintaining a Coanda effect.

d.	Slot diffuser/plenum:

1)	Diffuser: Frame and support bars shall be constructed of heavy gauge extruded aluminum. Form slots or use adjustable pattern controllers, to provide stable, horizontal air flow pattern over a wide range of operating conditions.

2)	Galvanized steel boot lined with 13 mm (1/2 inch) thick fiberglass conforming to NFPA 90A and complying with UL 181 for erosion. The internal lining shall be factory-fabricated, anti-microbial, and non-friable.

3)	Provide inlet connection diameter equal to duct diameter shown on drawings or provide transition coupling if necessary. Inlet duct and plenum size shall be as recommended by the manufacturer.

4)	Maximum pressure drop at design flow rate: 37 Pa

(0.15 inch W.G.)

2.	Linear Bar Grilles and Diffusers: Extruded aluminum, manufacturer's standard finish, and positive holding concealed fasteners.

a.	Margin Frame: Flat, 20 mm (3/4 inch) wide.

b.	Bars: Minimum 5 mm (3/16 inch) wide by 20 mm (3/4 inch) deep, zero deflection unless otherwise shown. Bar spacing shall be a minimum of 3 mm (1/8 inch) on center. Reinforce bars on 450 mm (18 inch) center for sidewall units and on 150 mm (6 inch) center for units installed in floor or sills.

c.	Provide opposed blade damper and equalizing or control grid where shown.

# 3.	Operating Room Air Distribution Devices:

a.	Devices shall consist of a non-aspirating perforated panel center air supply providing downward airflow over the operating table and fixed nonadjustable multiple slot perimeter panels surrounding the operating table area to provide an air curtain which shall be projected outward from the operating table area at not less than a five degree angle nor more than a 15 degree angle. Velocity of air distribution at operating table height shall not exceed 12 m/min (40 feet per minute) for the center supply or 15 m/min (50 feet per minute) for the air curtain. Perforated pressure plates shall be provided over the perimeter and center air distribution faces to equalize pressure and airflow throughout the system.

b.	All components of the system inside the operating room shall be fabricated of 1.0 mm (20 Gauge) thick 18-8 stainless steel (ASTM A167), No. 4 finish, and outside the operating room shall be of the manufacturer’s standard aluminum finish. All distribution components and pressure plates shall be attached to the face panels at both the perimeter and center. The face panels shall be retained with 1/4 turn fasteners. Plenums shall be supplied by the manufacturer and shall be sized to permit them to be easily wiped out by hand with germicidal solution for sterilization purposes and all horizontal corners of the plenums shall have a minimum radius of 20 mm (3/4 inch). Connecting elbows shall be radialized and be sized to permit manual sterilization of the plenums.

# 4.	Supply Registers: Double deflection type with horizontal face bars and opposed blade damper with removable key operator.

a.	Margin: Flat, 30 mm (1-1/4 inches) wide.

b.	Bar spacing: 20 mm (3/4 inch) maximum.

c.	Finish: Off white baked enamel for ceiling mounted units. Wall units shall have a prime coat for field painting, or shall be extruded with manufacturer's standard finish.

5.	Supply Grilles: Same as registers but without the opposed blade damper.

6.	Drum Louvers: Aluminum construction, drum louver, with pivoted blades and rotating drum to adjust length of throw and direction.

a.	Register shall have integral; face adjustable, opposed blade damper constructed of heavy gauge steel.  Damper shall be operable from the face of the register.  Units shall be nozzle type with adjustable discharge pattern.

7.	Jet Diffusers: Aluminum construction (nozzle and frame) suitable for wall or ceiling mounting or direct mounting on ducts.

D.	Return and Exhaust Registers and Grilles: Provide opposed blade damper without removable key operator for registers.

1.	Finish: Off-white baked enamel for ceiling mounted units. Wall units shall have a prime coat for field painting, or shall be extruded aluminum with manufacturer's standard aluminum finish.

2.	Standard Type: Fixed horizontal face bars set at 30 to 45 degrees, approximately 30 mm (1-1/4 inch) margin.

3.	Perforated Face Type: To match supply units.

4.	Grid Core Type: 13 mm by 13 mm (1/2 inch by 1/2 inch) core with 30 mm (1-1/4 inch) margin.

5.	Linear Type: To match supply units.

6.	Door Grilles: Are furnished with the doors.

7.	Egg Crate Grilles: Aluminum or Painted Steel 1/2 by 1/2 by 1/2 inch grid providing 90% free area.

a.	Heavy extruded aluminum frame shall have countersunk screw mounting.  Unless otherwise indicated, register blades and frame shall have factory applied white finish.

b.	Grille shall be suitable for duct or surface mounting as indicated on drawings.  All necessary appurtenances shall be provided to allow for mounting.

E.	Supply Registers in Psychiatric Rooms: Supply air registers shall be security type, steel with perforated faceplate, flat surface margin, extension sleeve, opposed blade damper and back mounting flanges. Faceplate shall be 5 mm (3/16 inch) (minimum) with 5x5 mm holes on 7 mm (3/16 by 3/16 inch holes on 9/32 inch) spacing and a minimum free area of 45 percent. Wall sleeve shall be 5 mm (3/16 inch) thick (minimum).

F.	Air Inlet Registers in Psychiatric Rooms: Return, exhaust, transfer and relief air registers shall be security type, steel with perforated faceplate, flat surface margin, wall sleeve, opposed blade damper and back mounting flanges. Faceplate shall be 5 mm (3/16 inch) (minimum) with 5x5 mm holes on 7 mm (3/16 by 3/16 inch holes on 9/32 inch) spacing and a minimum free area of 45 percent. Wall sleeve shall be 5 mm (3/16 inch) thick (minimum).

G.	Acoustic Transfer Grille: Aluminum, suitable for partition or wall mounting.

# 2.4 WIRE MESH GRILLE

A.	Fabricate grille with 2 x 2 mesh 13 mm (1/2 inch) galvanized steel or aluminum hardware cloth in a spot welded galvanized steel frame with approximately 40 mm (1-1/2 inch) margin.

B.	Use grilles where shown in unfinished areas such as mechanical rooms.

# 2.5 Filter return/exhaust grille

A.	Provide grille with in stream 1-inch deep MERV 4 filter and removable face.

1.	Finish: Off-white baked enamel for ceiling mounted units. Wall units shall have a prime coat for field painting, or shall be extruded aluminum with manufacturer's standard aluminum finish.  Stainless Steel shall be No. 4 finish.

2.	Standard Type: Fixed horizontal face bars set at 30 to 45 degrees, approximately 30 mm (1-1/4 inch) margin.

3.	Steel, Aluminum, or Stainless steel as scheduled.

4.	Standard face connected to a mounting frame with space for a throwaway filter.  Hold face closed by a locking screw.  Provide retaining clips to hold filter in place.  Provide fiberglass throwaway filter.

# part 3 - execution

3.1 INSTALLATION

A.	Comply with provisions of Section 23 05 11, COMMON WORK RESULTS FOR HVAC AND STEAM GENERATION, particularly regarding coordination with other trades and work in existing buildings.

B.	Protection and Cleaning: Protect equipment and materials against physical damage. Place equipment in first class operating condition, or return to source of supply for repair or replacement, as determined by Resident Engineer. Protect equipment during construction against entry of foreign matter to the inside and clean both inside and outside before operation and painting.

3.2 intake/ exhaust hoods exposed to wind velocity

Provide additional support and bracing to all exposed ductwork installed on the roof or outside the building to withstand wind velocity of 145 km/h (90 mph) or, in coastal areas, as defined in ASCE 7 Fig. 1.

# 3.3 testing, adjusting and balancing (tab)

Refer to Section 23 05 93, TESTING, ADJUSTING, and BALANCING FOR HVAC.

# 3.4 operating and performance tests

Refer to Section 23 05 11, COMMON WORK RESULTS FOR HVAC.

- - - E N D - - -